## Contents
Supplementary Material Contents
Techno-economic assessment of integrated floating photovoltaic and small-scale pumped hydro storage systems: A case study of the Te Mārua reservoirs in Wellington
1 | Literature Review
Studies on FPV-PHS integration, piloting integrated FPV-PHS system
2 | FPV Array Modelling
PVSyst irradiance and losses
3 | FPV Tech. Analysis
Calculation before PVSyst & after PVSyst Simulatio
4 | PHS Tech. Analysis
Calculation for volume discharge and proposed upper resorvior
5 | FPV 60 Years
NPV, IRR, and LCOE info
6 | Scenario 1
NPV, IRR, and LCOE info
7 | Scenario 2
NPV, IRR, and LCOE information regarding FPV 50% Energy(MWh) use to pump unergy using LCOE as PPA
8 | FPV Sensitivity
Sensitivity analysis results
9 | PSH Sensitivity
Sensitivity analysis results

## Literature review
Literature review
Identified gaps in literature
International Studies on FPV-PHS Integration
Study | Location / Context | Integration Type | Methodology | Key Findings / Contributions
Du et al. (2020) | China | FPV + PHS | Techno-economic modelling (HOMER + MATLAB) | Demonstrated economic feasibility of FPV-PHS integration with reservoir-based storage; highlighted synergies for peak shaving.
Uehara et al. (2022) | Japan (dam reservoir) | FPV + PHS | Real-world case assessment + economic analysis | Quantified energy output and financial returns; supported co-location on dam reservoirs.
Cazzaniga et al. (2018) | Italy | FPV only (mentions PHS potential) | Design & performance analysis | Emphasized FPV’s cooling effect, enhanced efficiency, and potential for coupling with hydro systems.
Pimenta et al. (2015) | Germany (theoretical framework) | Solar + PHS (terrestrial) | High-res simulation using real data | Proposed a hybrid model that supports solar and PHS integration in temperate climates.
Rehman et al. (2015) | Global review | PHS with renewables (incl. PV) | Technological review | Provided a broad foundation for understanding technical feasibility of PHS coupling with intermittent renewables.
Countries Adopting or Piloting Integrated FPV–PHS Systems
Country / Location | Project Name / Site | System Size (Power Generation) | Type of PHS | Scale | Key Features / Notes
China | Longyangxia Dam Reservoir FPV-PHS | ~40 MW (FPV) + ~320 MW (PHS) | Large-scale PHS | Large-scale | One of the largest integrated FPV-PHS systems globally; high efficiency; significant water surface area used
South Korea | Hongcheon FPV-PHS Pilot | ~1 MW (FPV) + ~5 MW (PHS) | Small-scale PHS | Pilot/Demo | Pilot project; research-driven; aims to optimize FPV-PHS synergy for grid stability
Japan | Lake Biwa Floating Solar + PHS | ~13 MW (FPV) + PHS under study | Medium-scale PHS | Medium-scale | Integrates FPV with existing reservoir PHS; environmental impact minimized
India | Telangana FPV + PHS Hybrid Project | ~10 MW (FPV) + ~30 MW (PHS) | Medium-scale PHS | Medium-scale | Government-backed hybrid renewable initiative; cost-effective and land-saving
USA | California FPV-PHS Demonstration | ~5 MW (FPV) + ~20 MW (PHS) | Small to medium PHS | Pilot/Demo | Focus on renewable integration and peak load management; pilot phase
France | Pompignac Reservoir FPV-PHS Pilot | ~2 MW (FPV) + PHS under planning | Small-scale PHS | Pilot/Demo | Focus on reducing land use and enhancing reservoir utility
Singapore | Tengeh Reservoir Floating Solar + Storage | ~60 MW (FPV) + Battery Storage | Battery storage hybrid | Medium-scale | Combining FPV with battery storage instead of PHS due to geography; innovative integration

## FPV array modelling
System design modelling and simulation
Floating photovoltaic (FPV) array modelling
Solar irridance data, temperature data, and loss diagram
Source: Pvsyst
Project: North Facing
Project: North Facing

## FPV Tech analysis
Results and discussion
Technical analysis
Available Surface Area at Te Marua (Lower Reservoir) - North Facing; Calculation without PV Syst
Lakes | Area (m^2) | Panel Area (m^2) | PV Type |  | Panel Tilt (°) | Tilt Type | PV Panel Rating (W) | PV Capacity (kW) | PV Modules | Installation Area (m^2) | Lake Area Used (%)
Lake 1 | 136806.45 | 3 | Bifacial Monocrystallin |  | 10 | North-Facing | 600 | 4000 | 6666.6667 | 20000 | 14.62%
Lake 2 | 176913.96 | 3 | Bifacial Monocrystallin |  | 10 | North-Facing | 600 | 6000 | 10000 | 30000 | 16.96%
Combine | 313720.41 | 3 | Bifacial Monocrystallin |  | 10 | North-Facing | 600 | 10000 | 16666.6667 | 50000 | 15.94%
Available Surface Area at Te Marua (Lower Reservoir) - East-West-Facing; Calculation without PV Syst
Lakes | Area (m^2) | Panel Area (m^2) | PV Type |  | Panel Tilt (°) | Tilt Type | PV Panel Rating (W) | PV Capacity (kW) | PV Modules | Installation Area (m^2) | Lake Area Used (%)
Lake 1 | 136806.45 | 3 | Bifacial Monocrystallin |  | 10 | East-West Facing | 600 | 4000 | 6666.6667 | 20000 | 14.62%
Lake 2 | 176913.96 | 3 | Bifacial Monocrystallin |  | 10 | East-West Facing | 600 | 6000 | 10000 | 30000 | 16.96%
Combine | 313720.41 | 3 | Bifacial Monocrystallin |  | 10 | East-West Facing | 600 | 10000 | 16666.6667 | 50000 | 15.94%
PVSyst Modelling Results
Option 1 : 10 MW(DC) North Facing Array |  |  |  | Option 2 : 10 MW(DC) East-West Facing Array
Parameter | PVsyst Results | Units |  | Parameter | PVsyst Results | Units
DC Capacity | 10 | MWp |  | DC Capacity | 10 | MWp
AC Capacity | 8.3333 | MVA |  | AC Capacity | 8.3333 | MVA
DC/AC Ratio | 1.2 | Ratio |  | DC/AC Ratio | 1.2 | Ratio
Floating Pontoon | Xiamen Mibet/Ciel & Terre |  |  | Floating Pontoon | Zimmerman (ZIM) PV Floating
PV Modules | Jinko 600W | Type |  | PV Modules | Jinko 600W | Type
No. Modules | 16659 | Panels |  | No. Modules | 16656 | Panels
Inverter Capacity | 4.4MVA SMA Skid | Inverter |  | Inverter Capacity | 4.4MVA SMA Skid | Inverter
No.Inverter | 2 | Inverter |  | No.Inverter | 2 | Inverter
Panel Tilt | 10 | deg |  | Panel Tilt | 10 | deg
Energy Generated | 14482 | MWh/year |  | Energy Generated | 13204 | MWh/Year
Array Losses | 0.43 | kWh/day |  | Array Losses | 0.4 | kWh/day
System Losses | 0.06 | kWh/day |  | System Losses | 0.05 | kWh/day
Total Area Covered | 45021 | m^2 |  | Total Area Covered | 46589 | m^2
Energy Performance (North-Facing) is
8.825% | Higher than East-West Facing

## PHS Tech analysis
Results and discussion
Technical analysis
Proposed PHS setup with cost estimation - calculated daily volume (m^3) discharge
Hydro Power Basic Calculation | [8 empty] | Penstock Diameter |  |  | Daily Water Discharge
Option | Turbine | Capacity (MW) | Efficiency (n) | Head (m) | Density (p) | Gravity (g) (m/s^2) | PS Length (m) | Max. Power Capicity | Flow Rate (Q) (m^3/s) | Velocity (m/s) | Diameter | Discharge Time (h) | Discharge Volume (m^3)
Option 1 | Francis | 5 | 80% | 160 | 1000 | 9.81 | 1000 | 7.8064 | 3.9819 | 6.2169 | 0.90306 | 10 | 143348.6239
| Francis | 5 | 80% | 160 | 1000 | 9.81 | 1000 | 7.8064 | 3.9819 | 6.2169 | 0.90306 | 10 | 143348.6239
Option.2 | Francis | 10 | 80% | 160 | 1000 | 9.81 | 1000 | 7.8064 | 7.9638 | 6.2169 | 1.2771 | 10 | 286697.2477
PHS storage capacity utilisation (%)
Te Marua Current Capicity (Lower Resorvior) |  |  |  | PSH to use 10% of Storage Capacity (m^3)
Lakes | Area (m^2) | Depth (m) | Capacity (ML) | Capacity (m^3) | 10% (m^3) | Drop Level Est.(m) |  |  | Formulas Used
Lake 1 | 136806.45 | 16 | 1460.86 | 1460860.0298 | 146086.003 | 1.0678 |  |  | Power
Lake 2 | 176913.96 | 16 | 1889.14 | 1889139.9702 | 188913.997 | 1.0678 |  |  | Flow Rate
Combine | 313720.41 | 16 | 3350 | 3350000 | 335000 | 1.0678
Proposed upper reservior - Lake 3
Lakes |  | Area (m^2) | Depth (m) | Capacity (ML) | Capacity (m^3)
Option 1 | Lake 3 | 61162 | 10 | 860.0917 | 860091.7431
Option 2 | Lake 3 | 53755.7339 | 16 | 860.0917 | 860091.7431
PHS technical data
Key Operating Parameter |  |  | Value | Units
Nameplate capacity |  |  | 10 | MW
Turbine type |  |  | Francis
Full pumping generation cycle |  |  | 10 | h
Full generation cycle |  |  | 10 | h
Total storage capacity |  |  | 300 | MWh
Ratio of pumping to generation cycle time |  |  | 1
Maximum generation output (at HV terminals) |  |  | 10 | MW
Maximum generation net water head |  |  | 160 | m
Maximum pump draw (at HV terminals) |  |  | 11 | MW
Maximum pump draw net water head |  |  | 160 | m
Minimum generation net water head |  |  | 155 | m
Minimum pump draw net water head |  |  | 9.6875 | MW
Head to Length Ratio |  |  | 0.16 | >0.1
Round Tripl efficiency |  |  | 80% | %
Note on B7: Kerry Pep: typical range of effiency 85% - 92%
Note on K7: Kerry Pep: NREL on PSH formula on Velocity was use to calculate the velocity (ft/s) (V=0.0074*Head+16.512)
Note on L7: Kerry Pep: NREL on PSH formula on Diameter was use to calculate the Diameter D=Sqrt(4*Q/V*pi)
Note on B8: Kerry Pep: typical range of effiency 85% - 92%
Note on K8: Kerry Pep: NREL on PSH formula on Velocity was use to calculate the velocity (ft/s) (V=0.0074*Head+16.512)
Note on L8: Kerry Pep: Diameter was use to calculate the Diameter D=Sqrt(4*Q/V*pi)
Note on B9: Kerry Pep: typical range of effiency 85% - 92%
Note on K9: Kerry Pep: NREL on PSH formula on Velocity was use to calculate the velocity (ft/s) (V=0.0074*Head+16.512)
Note on L9: Kerry Pep: Diameter was use to calculate the Diameter D=Sqrt(4*Q/V*pi)
Note on G14: Kerry Pep: Using the cubic formula (V=Area*Heigh) just to get an estimate on depth changing.
Note on G15: Kerry Pep: Using the cubic formula (V=Area*Heigh) just to get an estimate on depth changing.
Note on G16: Kerry Pep: Using the cubic formula (V=Area*Heigh) just to get an estimate on depth changing.
Note on F20: Kerry Pep: Volume is 3 x the daily discharge storage to be operated for 10Hrs
Note on F21: Kerry Pep: Volume is 3 x the daily discharge storage to be operated for 10Hrs
Note on D26: Kerry Pep: Reversible (vertical axis)
Note on D27: Kerry Pep: 10 hours (continuous from Minimul Operating Level (MOL) to Full Supply Level (FSL)) at nameplate capacity
Note on D28: Kerry Pep: 10 hours (continuous from FSL to MOL) at nameplate capacity
Note on D29: Kerry Pep: 300 MWh at nameplate capacity, 80 MWh guaranteed for 8 hours
Note on D33: Kerry Pep: assuming the power factor 0.9
Note on D37: Kerry Pep: According to site visit estimate
P
P=ρ.𝑔.𝑉.𝐻.ƞ
Q=𝑃/ρ.𝑔.𝑉.𝐻.ƞ

## FPV 30 Years (hidden)
Solar Project Costings
Unit
Plant Capacity | 10 | MWDC
Annual Generation | 14437 | MWh/year
CAPEX (USD) | 1270 | per kW
OPEX (USD) | 18 | per kW-Year
Inflation Factor | 3% | %
Degradtion Rate | 0.5% | %
Discounted Rate | 6% | %
Conversion to USD | 1.7 | NZD
Period | 30 | Years
LCOE/PPA | 0.14625 | $/kWh
Pro Forma
Period |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
NPV
PV Degradation Rate |  |  |  |  | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5%
Electricity Production (kWh) |  |  | 187891425.657 |  | 14364815 | 14292990.925 | 14221525.9704 | 14150418.3405 | 14079666.2488 | 14009267.9176 | 13939221.578 | 13869525.4701 | 13800177.8427 | 13731176.9535 | 13662521.0688 | 13594208.4634 | 13526237.4211 | 13458606.234 | 13391313.2028 | 13324356.6368 | 13257734.8536 | 13191446.1794 | 13125488.9485 | 13059861.5037 | 12994562.1962 | 12929589.3852 | 12864941.4383 | 12800616.7311 | 12736613.6475 | 12672930.5792 | 12609565.9263 | 12546518.0967 | 12483785.5062 | 12421366.5787
Inflation Factor |  |  |  |  | 1 | 1.03 | 1.0609 | 1.0927 | 1.1255 | 1.1593 | 1.1941 | 1.2299 | 1.2668 | 1.3048 | 1.3439 | 1.3842 | 1.4258 | 1.4685 | 1.5126 | 1.558 | 1.6047 | 1.6528 | 1.7024 | 1.7535 | 1.8061 | 1.8603 | 1.9161 | 1.9736 | 2.0328 | 2.0938 | 2.1566 | 2.2213 | 2.2879 | 2.3566
LCOE/PPA |  |  |  | 0 | 0.14625 | 0.15064 | 0.15516 | 0.15981 | 0.16461 | 0.16955 | 0.17463 | 0.17987 | 0.18527 | 0.19082 | 0.19655 | 0.20245 | 0.20852 | 0.21477 | 0.22122 | 0.22785 | 0.23469 | 0.24173 | 0.24898 | 0.25645 | 0.26415 | 0.27207 | 0.28023 | 0.28864 | 0.2973 | 0.30622 | 0.3154 | 0.32487 | 0.33461 | 0.34465
Total Revenues |  |  | 38036392.9134 | 0 | 2100873.0725 | 2153079.7684 | 2206583.8006 | 2261417.4081 | 2317613.6307 | 2375206.3294 | 2434230.2067 | 2494720.8273 | 2556714.6399 | 2620248.9987 | 2685362.1863 | 2752093.4366 | 2820482.9585 | 2890571.9601 | 2962402.6733 | 3036018.3797 | 3111463.4364 | 3188783.3028 | 3268024.5679 | 3349234.9784 | 3432463.4676 | 3517760.1848 | 3605176.5254 | 3694765.162 | 3786580.0763 | 3880676.5912 | 3977111.4045 | 4075942.6229 | 4177229.7971 | 4281033.9575
Solar PV CAPEX |  | 21590000 | 21590000 | 21590000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar PV OPEX |  | 306000 | 5889367.9365 | 0 | 306000 | 315180 | 324635.4 | 334374.462 | 344405.6959 | 354737.8667 | 365380.0027 | 376341.4028 | 387631.6449 | 399260.5943 | 411238.4121 | 423575.5644 | 436282.8314 | 449371.3163 | 462852.4558 | 476738.0295 | 491040.1704 | 505771.3755 | 520944.5167 | 536572.8522 | 552670.0378 | 569250.1389 | 586327.6431 | 603917.4724 | 622034.9966 | 640696.0465 | 659916.9279 | 679714.4357 | 700105.8688 | 721109.0448
Net Cash Flow |  |  |  | -21590000 | 1794873.0725 | 1837899.7684 | 1881948.4006 | 1927042.9461 | 1973207.9348 | 2020468.4627 | 2068850.204 | 2118379.4245 | 2169082.995 | 2220988.4044 | 2274123.7742 | 2328517.8722 | 2384200.1272 | 2441200.6437 | 2499550.2175 | 2559280.3502 | 2620423.2661 | 2683011.9273 | 2747080.0512 | 2812662.1262 | 2879793.4298 | 2948510.0459 | 3018848.8823 | 3090847.6896 | 3164545.0797 | 3239980.5447 | 3317194.4766 | 3396228.1872 | 3477123.9283 | 3559924.9127
Cumulative Cash Flow |  |  |  | -21590000 | -19795126.9275 | -17957227.1591 | -16075278.7584 | -14148235.8123 | -12175027.8775 | -10154559.4148 | -8085709.2109 | -5967329.7864 | -3798246.7914 | -1577258.3869 | 696865.3873 | 3025383.2595 | 5409583.3866 | 7850784.0304 | 10350334.2478 | 12909614.598 | 15530037.8641 | 18213049.7914 | 20960129.8426 | 23772791.9688 | 26652585.3986 | 29601095.4444 | 32619944.3267 | 35710792.0164 | 38875337.0961 | 42115317.6408 | 45432512.1175 | 48828740.3047 | 52305864.233 | 55865789.1457
NPV |  |  | 10557024.9768 | bar: 0
IRR |  |  | 4.531% | bar: 0
Payback Period |  |  | 10.6936 | 0: Years
LCOE |  |  | 0.14625 | 0: $/kWh
LCOE |  |  | 146.2513 | 0: $/MWh
PPA |  |  | 165 | 0: $/MWh
Note on D5: Kerry Pep: According to PV Syst when tilting at 15 degree facing north
Note on D11: Kerry Pep: Current Rate
Note on B21: Kerry Pep: According to IRENA Renewable Power Generation Cost Report 2021. Degradation of Wind Turbine is 0.5

## FPV 60 Years
Results and discussion
Economic analysis
Solar Project Costings
Unit
Plant Capacity | 10 | MWDC |  |  | FPV Economical Summery Results
Annual Generation | 14437 | MWh/year |  |  | FPV Period (Years) |  | 30 | 60
CAPEX (USD) | 1270 | per kW |  |  | Discount Rate |  | 6% | 6%
OPEX (USD) | 18 | per kW-Year |  |  | Energy Generated (MWh) |  | 187891.4257 | 218753.5018
Inflation Factor | 3% | % |  |  | PPA=LCOE ($/MWh) |  | 146.2513 | 150
Degradtion Rate | 0.5% | % |  |  | Revenues ($) |  | 38036392.9134 | 54602863.2426
Discounted Rate | 6% | % |  |  | CAPEX |  | 21590000 | 24249696.5045
Conversion to USD | 1.7 | NZD |  |  | OPEX |  | 5889367.9365 | 8307838.6366
Period (2nd Life) | 60 | Years |  |  | NPV ($) |  | 10557024.9768 | 22045328.1015
LCOE/PPA | 0.14883 | $/kWh |  |  | IRR (%) |  | 4.5% | 5%
[5 empty] | Payback Period (Years) |  | 10.6936 | 10.7
[5 empty] | LCOE ($/kWh) |  | 0.14625 | 0.15
Pro Forma
Period |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61
NPV
PV Degradation Rate |  |  |  |  | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5%
Electricity Production (kWh) |  |  | 218753501.8062 |  | 14364815 | 14292990.925 | 14221525.9704 | 14150418.3405 | 14079666.2488 | 14009267.9176 | 13939221.578 | 13869525.4701 | 13800177.8427 | 13731176.9535 | 13662521.0688 | 13594208.4634 | 13526237.4211 | 13458606.234 | 13391313.2028 | 13324356.6368 | 13257734.8536 | 13191446.1794 | 13125488.9485 | 13059861.5037 | 12994562.1962 | 12929589.3852 | 12864941.4383 | 12800616.7311 | 12736613.6475 | 12672930.5792 | 12609565.9263 | 12546518.0967 | 12483785.5062 | 12421366.5787 | 0 | 14364815 | 14292990.925 | 14221525.9704 | 14150418.3405 | 14079666.2488 | 14009267.9176 | 13939221.578 | 13869525.4701 | 13800177.8427 | 13731176.9535 | 13662521.0688 | 13594208.4634 | 13526237.4211 | 13458606.234 | 13391313.2028 | 13324356.6368 | 13257734.8536 | 13191446.1794 | 13125488.9485 | 13059861.5037 | 12994562.1962 | 12929589.3852 | 12864941.4383 | 12800616.7311 | 12736613.6475 | 12672930.5792 | 12609565.9263 | 12546518.0967 | 12483785.5062 | 12421366.5787
Inflation Factor |  |  |  |  | 1 | 1.03 | 1.0609 | 1.0927 | 1.1255 | 1.1593 | 1.1941 | 1.2299 | 1.2668 | 1.3048 | 1.3439 | 1.3842 | 1.4258 | 1.4685 | 1.5126 | 1.558 | 1.6047 | 1.6528 | 1.7024 | 1.7535 | 1.8061 | 1.8603 | 1.9161 | 1.9736 | 2.0328 | 2.0938 | 2.1566 | 2.2213 | 2.2879 | 2.3566 | 0 | 2.5001 | 2.5751 | 2.6523 | 2.7319 | 2.8139 | 2.8983 | 2.9852 | 3.0748 | 3.167 | 3.262 | 3.3599 | 3.4607 | 3.5645 | 3.6715 | 3.7816 | 3.895 | 4.0119 | 4.1323 | 4.2562 | 4.3839 | 4.5154 | 4.6509 | 4.7904 | 4.9341 | 5.0821 | 5.2346 | 5.3917 | 5.5534 | 5.72 | 5.8916
LCOE/PPA |  |  |  | 0 | 0.14883 | 0.1533 | 0.1579 | 0.16263 | 0.16751 | 0.17254 | 0.17771 | 0.18304 | 0.18854 | 0.19419 | 0.20002 | 0.20602 | 0.2122 | 0.21856 | 0.22512 | 0.23188 | 0.23883 | 0.246 | 0.25338 | 0.26098 | 0.26881 | 0.27687 | 0.28518 | 0.29373 | 0.30254 | 0.31162 | 0.32097 | 0.3306 | 0.34052 | 0.35073 | 0 | 0.37209 | 0.38325 | 0.39475 | 0.4066 | 0.41879 | 0.43136 | 0.4443 | 0.45763 | 0.47136 | 0.4855 | 0.50006 | 0.51506 | 0.53051 | 0.54643 | 0.56282 | 0.57971 | 0.5971 | 0.61501 | 0.63346 | 0.65247 | 0.67204 | 0.6922 | 0.71297 | 0.73436 | 0.75639 | 0.77908 | 0.80245 | 0.82652 | 0.85132 | 0.87686
Total Revenues |  |  | 54602863.2426 | 0 | 2137945.0628 | 2191072.9976 | 2245521.1616 | 2301322.3625 | 2358510.2232 | 2417119.2022 | 2477184.6144 | 2538742.6521 | 2601830.407 | 2666485.8926 | 2732748.067 | 2800656.8565 | 2870253.1794 | 2941578.9709 | 3014677.2083 | 3089591.9369 | 3166368.2966 | 3245052.5487 | 3325692.1046 | 3408335.5534 | 3493032.6919 | 3579834.5543 | 3668793.4429 | 3759962.96 | 3853398.0395 | 3949154.9808 | 4047291.4821 | 4147866.6754 | 4250941.1623 | 4356577.0502 | 0 | 5345034.4309 | 5477858.5365 | 5613983.3211 | 5753490.8067 | 5896465.0532 | 6042992.2098 | 6193160.5662 | 6347060.6063 | 6504785.0623 | 6666428.9711 | 6832089.7311 | 7001867.1609 | 7175863.5598 | 7354183.7693 | 7536935.236 | 7724228.0766 | 7916175.1443 | 8112892.0966 | 8314497.4652 | 8521112.7272 | 8732862.3785 | 8949874.0086 | 9172278.3777 | 9400209.4954 | 9633804.7014 | 9873204.7482 | 10118553.8862 | 10369999.9503 | 10627694.449 | 10891792.6561
Solar PV CAPEX |  | 21590000 | 24249696.5045 | 21590000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16192500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar PV OPEX |  | 306000 | 8307838.6366 | 0 | 306000 | 315180 | 324635.4 | 334374.462 | 344405.6959 | 354737.8667 | 365380.0027 | 376341.4028 | 387631.6449 | 399260.5943 | 411238.4121 | 423575.5644 | 436282.8314 | 449371.3163 | 462852.4558 | 476738.0295 | 491040.1704 | 505771.3755 | 520944.5167 | 536572.8522 | 552670.0378 | 569250.1389 | 586327.6431 | 603917.4724 | 622034.9966 | 640696.0465 | 659916.9279 | 679714.4357 | 700105.8688 | 721109.0448 | 0 | 765024.5857 | 787975.3232 | 811614.5829 | 835963.0204 | 861041.911 | 886873.1684 | 913479.3634 | 940883.7443 | 969110.2567 | 998183.5644 | 1028129.0713 | 1058972.9434 | 1090742.1317 | 1123464.3957 | 1157168.3275 | 1191883.3774 | 1227639.8787 | 1264469.0751 | 1302403.1473 | 1341475.2417 | 1381719.499 | 1423171.0839 | 1465866.2165 | 1509842.203 | 1555137.469 | 1601791.5931 | 1649845.3409 | 1699340.7011 | 1750320.9222 | 1802830.5498
Net Cash Flow |  |  |  | -21590000 | 1831945.0628 | 1875892.9976 | 1920885.7616 | 1966947.9005 | 2014104.5273 | 2062381.3355 | 2111804.6117 | 2162401.2492 | 2214198.7621 | 2267225.2983 | 2321509.6549 | 2377081.292 | 2433970.348 | 2492207.6546 | 2551824.7525 | 2612853.9074 | 2675328.1262 | 2739281.1732 | 2804747.5878 | 2871762.7011 | 2940362.6541 | 3010584.4153 | 3082465.7998 | 3156045.4876 | 3231363.043 | 3308458.9343 | 3387374.5542 | 3468152.2397 | 3550835.2935 | 3635468.0054 | -16192500 | 4580009.8452 | 4689883.2133 | 4802368.7382 | 4917527.7862 | 5035423.1422 | 5156119.0414 | 5279681.2028 | 5406176.8619 | 5535674.8057 | 5668245.4068 | 5803960.6598 | 5942894.2175 | 6085121.4281 | 6230719.3736 | 6379766.9084 | 6532344.6992 | 6688535.2656 | 6848423.0216 | 7012094.3179 | 7179637.4855 | 7351142.8795 | 7526702.9247 | 7706412.1613 | 7890367.2924 | 8078667.2323 | 8271413.1551 | 8468708.5453 | 8670659.2491 | 8877373.5268 | 9088962.1062
Cumulative Cash Flow |  |  |  | -21590000 | -19758054.9372 | -17882161.9396 | -15961276.178 | -13994328.2775 | -11980223.7502 | -9917842.4147 | -7806037.803 | -5643636.5538 | -3429437.7917 | -1162212.4934 | 1159297.1615 | 3536378.4536 | 5970348.8016 | 8462556.4561 | 11014381.2086 | 13627235.1161 | 16302563.2422 | 19041844.4155 | 21846592.0033 | 24718354.7044 | 27658717.3585 | 30669301.7738 | 33751767.5736 | 36907813.0612 | 40139176.1041 | 43447635.0385 | 46835009.5927 | 50303161.8324 | 53853997.126 | 57489465.1313 | 41296965.1313 | 45876974.9766 | 50566858.1898 | 55369226.928 | 60286754.7143 | 65322177.8564 | 70478296.8979 | 75757978.1006 | 81164154.9626 | 86699829.7683 | 92368075.1751 | 98172035.8348 | 104114930.0523 | 110200051.4804 | 116430770.854 | 122810537.7625 | 129342882.4617 | 136031417.7273 | 142879840.7488 | 149891935.0667 | 157071572.5522 | 164422715.4317 | 171949418.3564 | 179655830.5177 | 187546197.8101 | 195624865.0424 | 203896278.1975 | 212364986.7428 | 221035645.9919 | 229913019.5187 | 239001981.625
NPV |  |  | 22045328.1015 | bar: 0
IRR |  |  | 4.905% | bar: 0
Payback Period |  |  | 10.6964 | 0: Years
LCOE |  |  | 0.14883 | 0: $/kWh
LCOE |  |  | 148.8321 | 0: $/MWh
Note on C7: Kerry Pep: According to PV Syst when tilting at 15 degree facing north
Note on C13: Kerry Pep: Current Rate
Note on A23: Kerry Pep: According to IRENA Renewable Power Generation Cost Report 2021. Degradation of Wind Turbine is 0.5

## Scenario 1
Results and discussion
Economic analysis
Project Costings
Inputs |  |  | Unit
| Plant Capacity | 10 | MW |  | PHS Economical Summery Results
| No. of Cycles/Year | 365 | Days |  | PSH Period (Years) |  | 60
| PSH Operational Hours | 10 | hours |  | Discount Rate |  | 6%
| Round Trip Efficiency | 80% | % |  | Energy Generated (MWh) |  | 580697.3107
| Operational Losses | 0.1% | % |  | Energy for Pumping (MWh) |  | 736627.7739
| CAPEX (USD) | 3000 | per kW |  | PPA ($/MWH) |  | 200
| OPEX (USD) | 20 | per kW-Year |  | Revenues ($) |  | 195491801.3851
| Discount Rate: | 6% | % |  | CAPEX |  | 51000000
| Conversion to USD | 1.7 | NZD |  | OPEX |  | 9309199.4786
| Inflation Factor | 3% | % |  | Buying Energy @ off-peak ($/MWh) |  | $70.00
| Period | 60 | years |  | Pumping Energy Cost |  | 87444870.1022
| Grid Cost Off-Peak | 70 | $/MWh |  | NPV ($) |  | 47737731.8043
| Grid Cost Peak | 200 | $/MWh |  | IRR (%) |  | 9.788%
Derived Energy |  |  |  |  | Payback Period (Years) |  | 11.6576
| Annual Generation | 36500 | MWh/year |  | LCOE ($/kWh) |  | 0.25444
| Energy Needed for Pumping | 45625 | MWh/year |  | COSE (Cost of Stored Energy) ($/MWh) |  | 254.4425
Pro Forma
| Period |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60
Energy |  |  |  | NPV
| Operational Losses |  |  |  |  | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1%
| Electricity Production (kWh) |  |  | 580697310.6921 |  | 36463500 | 36427036.5 | 36390609.4635 | 36354218.854 | 36317864.6352 | 36281546.7705 | 36245265.2238 | 36209019.9586 | 36172810.9386 | 36136638.1277 | 36100501.4895 | 36064400.988 | 36028336.5871 | 35992308.2505 | 35956315.9422 | 35920359.6263 | 35884439.2666 | 35848554.8274 | 35812706.2726 | 35776893.5663 | 35741116.6727 | 35705375.556 | 35669670.1805 | 35634000.5103 | 35598366.5098 | 35562768.1433 | 35527205.3751 | 35491678.1698 | 35456186.4916 | 35420730.3051 | 35385309.5748 | 35349924.2652 | 35314574.341 | 35279259.7666 | 35243980.5068 | 35208736.5263 | 35173527.7898 | 35138354.262 | 35103215.9078 | 35068112.6919 | 35033044.5792 | 34998011.5346 | 34963013.5231 | 34928050.5095 | 34893122.459 | 34858229.3366 | 34823371.1072 | 34788547.7361 | 34753759.1884 | 34719005.4292 | 34684286.4238 | 34649602.1373 | 34614952.5352 | 34580337.5827 | 34545757.2451 | 34511211.4878 | 34476700.2764 | 34442223.5761 | 34407781.3525 | 34373373.5711
| Energy for Pumping (kWh) |  |  | 736627773.9124 |  | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375
| Inflation Factor |  |  |  |  | 1 | 1.03 | 1.0609 | 1.0927 | 1.1255 | 1.1593 | 1.1941 | 1.2299 | 1.2668 | 1.3048 | 1.3439 | 1.3842 | 1.4258 | 1.4685 | 1.5126 | 1.558 | 1.6047 | 1.6528 | 1.7024 | 1.7535 | 1.8061 | 1.8603 | 1.9161 | 1.9736 | 2.0328 | 2.0938 | 2.1566 | 2.2213 | 2.2879 | 2.3566 | 2.4273 | 2.5001 | 2.5751 | 2.6523 | 2.7319 | 2.8139 | 2.8983 | 2.9852 | 3.0748 | 3.167 | 3.262 | 3.3599 | 3.4607 | 3.5645 | 3.6715 | 3.7816 | 3.895 | 4.0119 | 4.1323 | 4.2562 | 4.3839 | 4.5154 | 4.6509 | 4.7904 | 4.9341 | 5.0821 | 5.2346 | 5.3917 | 5.5534 | 5.72
| LCOE/PPA ($/kWh) |  |  |  | 0 | 0.2 | 0.206 | 0.21218 | 0.21855 | 0.2251 | 0.23185 | 0.23881 | 0.24597 | 0.25335 | 0.26095 | 0.26878 | 0.27685 | 0.28515 | 0.29371 | 0.30252 | 0.31159 | 0.32094 | 0.33057 | 0.34049 | 0.3507 | 0.36122 | 0.37206 | 0.38322 | 0.39472 | 0.40656 | 0.41876 | 0.43132 | 0.44426 | 0.45759 | 0.47131 | 0.48545 | 0.50002 | 0.51502 | 0.53047 | 0.54638 | 0.56277 | 0.57966 | 0.59705 | 0.61496 | 0.63341 | 0.65241 | 0.67198 | 0.69214 | 0.7129 | 0.73429 | 0.75632 | 0.77901 | 0.80238 | 0.82645 | 0.85124 | 0.87678 | 0.90308 | 0.93018 | 0.95808 | 0.98682 | 1.0164 | 1.0469 | 1.0783 | 1.1107 | 1.144
| Total Energy Revenues |  |  | 195491801.3851 | 0 | 7292700 | 7503969.519 | 7721359.516 | 7945047.3011 | 8175215.3215 | 8412051.3093 | 8655748.4358 | 8906505.4679 | 9164526.9313 | 9430023.2765 | 9703211.0509 | 9984313.075 | 10273558.6248 | 10571183.6181 | 10877430.8076 | 11192549.9781 | 11516798.1509 | 11850439.7934 | 12193747.0342 | 12546999.8858 | 12910486.4724 | 13284503.2655 | 13669355.3252 | 14065356.5489 | 14472829.9281 | 14892107.8112 | 15323532.1745 | 15767454.9015 | 16224238.07 | 16694254.2469 | 17177886.7925 | 17675530.1728 | 18187590.282 | 18714484.7724 | 19256643.3963 | 19814508.3555 | 20388534.6625 | 20979190.5117 | 21586957.6608 | 22212331.8243 | 22855823.0772 | 23517956.2718 | 24199271.4649 | 24900324.3593 | 25621686.756 | 26363947.0213 | 27127710.5665 | 27913600.3416 | 28722257.3435 | 29554341.1387 | 30410530.4015 | 31291523.4673 | 32198038.9021 | 33130816.0891 | 34090615.8312 | 35078220.9718 | 36094437.0334 | 37140092.8743 | 38216041.3648 | 39323160.0832
Fixed + Variable Cost
| PSH CAPEX |  | 51000000 | 51000000 | 51000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PSH O&M |  | 340000 | 9309199.4786 | 0 | 340000 | 350200 | 360706 | 371527.18 | 382672.9954 | 394153.1853 | 405977.7808 | 418157.1142 | 430701.8277 | 443622.8825 | 456931.569 | 470639.516 | 484758.7015 | 499301.4626 | 514280.5065 | 529708.9216 | 545600.1893 | 561968.195 | 578827.2408 | 596192.058 | 614077.8198 | 632500.1544 | 651475.159 | 671019.4138 | 691149.9962 | 711884.4961 | 733241.031 | 755238.2619 | 777895.4098 | 801232.272 | 825269.2402 | 850027.3174 | 875528.1369 | 901793.981 | 928847.8005 | 956713.2345 | 985414.6315 | 1014977.0705 | 1045426.3826 | 1076789.1741 | 1109092.8493 | 1142365.6348 | 1176636.6038 | 1211935.7019 | 1248293.773 | 1285742.5862 | 1324314.8637 | 1364044.3097 | 1404965.6389 | 1447114.6081 | 1490528.0464 | 1535243.8878 | 1581301.2044 | 1628740.2405 | 1677602.4477 | 1727930.5212 | 1779768.4368 | 1833161.4899 | 1888156.3346 | 1944801.0246
Annual Pumping Cost (PSH)
| Grid Off-Peak Cost |  | 3193750 | 87444870.1022 | 0 | 3193750 | 3289562.5 | 3388249.375 | 3489896.8563 | 3594593.7619 | 3702431.5748 | 3813504.522 | 3927909.6577 | 4045746.9474 | 4167119.3559 | 4292132.9365 | 4420896.9246 | 4553523.8324 | 4690129.5473 | 4830833.4338 | 4975758.4368 | 5125031.1899 | 5278782.1256 | 5437145.5893 | 5600259.957 | 5768267.7557 | 5941315.7884 | 6119555.262 | 6303141.9199 | 6492236.1775 | 6687003.2628 | 6887613.3607 | 7094241.7615 | 7307069.0144 | 7526281.0848 | 7752069.5174 | 7984631.6029 | 8224170.551 | 8470895.6675 | 8725022.5375 | 8986773.2136 | 9256376.4101 | 9534067.7024 | 9820089.7334 | 10114692.4254 | 10418133.1982 | 10730677.1941 | 11052597.51 | 11384175.4353 | 11725700.6983 | 12077471.7193 | 12439795.8709 | 12812989.747 | 13197379.4394 | 13593300.8226 | 14001099.8472 | 14421132.8427 | 14853766.8279 | 15299379.8328 | 15758361.2278 | 16231112.0646 | 16718045.4265 | 17219586.7893 | 17736174.393 | 18268259.6248
| Total Cost (CAPEX+O&M+Grid Off-Peak) |  |  | 147754069.5808
| Net Cash Flow/ Annual Margin |  |  | 47737731.8043 | -51000000 | 3758950 | 3864207.019 | 3972404.141 | 4083623.2649 | 4197948.5641 | 4315466.5493 | 4436266.1329 | 4560438.696 | 4688078.1562 | 4819281.0382 | 4954146.5454 | 5092776.6343 | 5235276.0909 | 5381752.6082 | 5532316.8674 | 5687082.6196 | 5846166.7718 | 6009689.4728 | 6177774.204 | 6350547.8707 | 6528140.8969 | 6710687.3228 | 6898324.9041 | 7091195.2152 | 7289443.7544 | 7493220.0522 | 7702677.7828 | 7917974.8781 | 8139273.6459 | 8366740.8901 | 8600548.0349 | 8840871.2526 | 9087891.594 | 9341795.1239 | 9602773.0583 | 9871021.9073 | 10146743.6209 | 10430145.7389 | 10721441.5448 | 11020850.2248 | 11328597.0297 | 11644913.4429 | 11970037.3512 | 12304213.2221 | 12647692.2847 | 13000732.7159 | 13363599.8319 | 13736566.285 | 14119912.2652 | 14513925.7081 | 14918902.5079 | 15335146.7369 | 15762970.8698 | 16202696.0158 | 16654652.1557 | 17119178.3861 | 17596623.1701 | 18087344.595 | 18591710.6372 | 19110099.4337
| Cumulative Cash Flow |  |  |  | -51000000 | -47241050 | -43376842.981 | -39404438.84 | -35320815.5751 | -31122867.011 | -26807400.4618 | -22371134.3289 | -17810695.6329 | -13122617.4766 | -8303336.4385 | -3349189.8931 | 1743586.7412 | 6978862.8321 | 12360615.4404 | 17892932.3077 | 23580014.9274 | 29426181.6991 | 35435871.172 | 41613645.376 | 47964193.2467 | 54492334.1436 | 61203021.4664 | 68101346.3705 | 75192541.5857 | 82481985.3401 | 89975205.3924 | 97677883.1751 | 105595858.0533 | 113735131.6992 | 122101872.5892 | 130702420.6241 | 139543291.8767 | 148631183.4707 | 157972978.5946 | 167575751.6529 | 177446773.5602 | 187593517.1812 | 198023662.92 | 208745104.4649 | 219765954.6896 | 231094551.7194 | 242739465.1622 | 254709502.5134 | 267013715.7355 | 279661408.0202 | 292662140.736 | 306025740.5679 | 319762306.8529 | 333882219.1181 | 348396144.8261 | 363315047.3341 | 378650194.0709 | 394413164.9407 | 410615860.9565 | 427270513.1122 | 444389691.4983 | 461986314.6684 | 480073659.2634 | 498665369.9006 | 517775469.3343
| NPV |  |  | 47737731.8043 | bar: 0
| IRR |  |  | 9.788% | bar: 0
| Payback Period |  |  | 11.6576 | 0: Years
| LCOE (Before Pumping) |  |  | 0.10386 | 0: $/kWh
| LCOE (Pumping) |  |  | 0.25444 | 0: $/kWh
| Cost of Stored Energy (COSE) | Grid Off-Peak |  | 254.4425 | 0: $/MWh
Note on D14: Kerry Pep: Current Rate
Note on B27: Kerry Pep: According to IRENA Renewable Power Generation Cost Report 2021. Degradation of Wind Turbine is 0.5

## Scenario 2
Results and discussion
Economic analysis
Project Costings
Inputs |  |  | Unit
| Plant Capacity | 10 | MW |  | PSH Economical Summery Results
| No. of Cycles/Year | 365 | Days |  | PSH Period (Years) |  | 60
| PSH Operational Hours | 10 | hours |  | Discount Rate |  | 6%
| Round Trip Efficiency | 80% | % |  | Energy Generated (MWh) |  | 580697.3107
| Operational Losses | 0.1% | % |  | Energy for Pumping (MWh) |  | 736627.7739
| CAPEX (USD) | 3000 | per kW |  | PPA ($/MWH) |  | 200
| OPEX (USD) | 20 | per kW-Year |  | Revenues ($) |  | 195491801.3851
| Discount Rate: | 6% | % |  | CAPEX |  | 51000000
| Conversion to USD | 1.7 | NZD |  | OPEX |  | 9309199.4786
| Inflation Factor | 3% | % |  | FPV Cost PPA = LCOE ($/MWh) |  | 149
| Period | 60 | years |  | Buying Energy @ off-peak ($/MWh) |  | $70.00
| FPV Cost PPA = LCOE | 148.8321 | $/MWh |  | Pumping Energy Cost |  | 136683867.105
| Grid Cost Off-Peak | 70 | $/MWh |  | NPV ($) |  | -1501265.1985
| Grid Cost Peak | 200 | $/MWh |  | IRR (%) |  | 5%
| FPV Pumping Rate | 50% |  |  | Payback Period (Years) |  | 21.13
| Grid Pumping Rate | 50% |  |  | LCOE ($/kWh) |  | 0.34
Derived Energy |  |  |  |  | COSE (Cost of Stored Energy) ($/MWh) |  | 339.24
| Annual Generation | 36500 | MWh/year
| Energy Needed for Pumping | 45625 | MWh/year
| FPV Pumping Enegy | 22812.5 | MWh/year
| Grid Pumping Energy | 22812.5 | MWh/year
Pro Forma
| Period |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60
Energy |  |  |  | NPV
| Operational Losses |  |  |  |  | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1% | 0.1%
| Electricity Production (kWh) |  |  | 580697310.6921 |  | 36463500 | 36427036.5 | 36390609.4635 | 36354218.854 | 36317864.6352 | 36281546.7705 | 36245265.2238 | 36209019.9586 | 36172810.9386 | 36136638.1277 | 36100501.4895 | 36064400.988 | 36028336.5871 | 35992308.2505 | 35956315.9422 | 35920359.6263 | 35884439.2666 | 35848554.8274 | 35812706.2726 | 35776893.5663 | 35741116.6727 | 35705375.556 | 35669670.1805 | 35634000.5103 | 35598366.5098 | 35562768.1433 | 35527205.3751 | 35491678.1698 | 35456186.4916 | 35420730.3051 | 35385309.5748 | 35349924.2652 | 35314574.341 | 35279259.7666 | 35243980.5068 | 35208736.5263 | 35173527.7898 | 35138354.262 | 35103215.9078 | 35068112.6919 | 35033044.5792 | 34998011.5346 | 34963013.5231 | 34928050.5095 | 34893122.459 | 34858229.3366 | 34823371.1072 | 34788547.7361 | 34753759.1884 | 34719005.4292 | 34684286.4238 | 34649602.1373 | 34614952.5352 | 34580337.5827 | 34545757.2451 | 34511211.4878 | 34476700.2764 | 34442223.5761 | 34407781.3525 | 34373373.5711
| Energy for Pumping (kWh) |  |  | 736627773.9124 |  | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375 | 45579375
| Inflation Factor |  |  |  |  | 1 | 1.03 | 1.0609 | 1.0927 | 1.1255 | 1.1593 | 1.1941 | 1.2299 | 1.2668 | 1.3048 | 1.3439 | 1.3842 | 1.4258 | 1.4685 | 1.5126 | 1.558 | 1.6047 | 1.6528 | 1.7024 | 1.7535 | 1.8061 | 1.8603 | 1.9161 | 1.9736 | 2.0328 | 2.0938 | 2.1566 | 2.2213 | 2.2879 | 2.3566 | 2.4273 | 2.5001 | 2.5751 | 2.6523 | 2.7319 | 2.8139 | 2.8983 | 2.9852 | 3.0748 | 3.167 | 3.262 | 3.3599 | 3.4607 | 3.5645 | 3.6715 | 3.7816 | 3.895 | 4.0119 | 4.1323 | 4.2562 | 4.3839 | 4.5154 | 4.6509 | 4.7904 | 4.9341 | 5.0821 | 5.2346 | 5.3917 | 5.5534 | 5.72
| LCOE/PPA ($/kWh) |  |  |  | 0 | 0.2 | 0.206 | 0.21218 | 0.21855 | 0.2251 | 0.23185 | 0.23881 | 0.24597 | 0.25335 | 0.26095 | 0.26878 | 0.27685 | 0.28515 | 0.29371 | 0.30252 | 0.31159 | 0.32094 | 0.33057 | 0.34049 | 0.3507 | 0.36122 | 0.37206 | 0.38322 | 0.39472 | 0.40656 | 0.41876 | 0.43132 | 0.44426 | 0.45759 | 0.47131 | 0.48545 | 0.50002 | 0.51502 | 0.53047 | 0.54638 | 0.56277 | 0.57966 | 0.59705 | 0.61496 | 0.63341 | 0.65241 | 0.67198 | 0.69214 | 0.7129 | 0.73429 | 0.75632 | 0.77901 | 0.80238 | 0.82645 | 0.85124 | 0.87678 | 0.90308 | 0.93018 | 0.95808 | 0.98682 | 1.0164 | 1.0469 | 1.0783 | 1.1107 | 1.144
| Total Energy Revenues |  |  | 195491801.3851 | 0 | 7292700 | 7503969.519 | 7721359.516 | 7945047.3011 | 8175215.3215 | 8412051.3093 | 8655748.4358 | 8906505.4679 | 9164526.9313 | 9430023.2765 | 9703211.0509 | 9984313.075 | 10273558.6248 | 10571183.6181 | 10877430.8076 | 11192549.9781 | 11516798.1509 | 11850439.7934 | 12193747.0342 | 12546999.8858 | 12910486.4724 | 13284503.2655 | 13669355.3252 | 14065356.5489 | 14472829.9281 | 14892107.8112 | 15323532.1745 | 15767454.9015 | 16224238.07 | 16694254.2469 | 17177886.7925 | 17675530.1728 | 18187590.282 | 18714484.7724 | 19256643.3963 | 19814508.3555 | 20388534.6625 | 20979190.5117 | 21586957.6608 | 22212331.8243 | 22855823.0772 | 23517956.2718 | 24199271.4649 | 24900324.3593 | 25621686.756 | 26363947.0213 | 27127710.5665 | 27913600.3416 | 28722257.3435 | 29554341.1387 | 30410530.4015 | 31291523.4673 | 32198038.9021 | 33130816.0891 | 34090615.8312 | 35078220.9718 | 36094437.0334 | 37140092.8743 | 38216041.3648 | 39323160.0832
Fixed + Variable Cost
| PSH CAPEX |  | 51000000 | 51000000 | 51000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PSH O&M |  | 340000 | 9309199.4786 | 0 | 340000 | 350200 | 360706 | 371527.18 | 382672.9954 | 394153.1853 | 405977.7808 | 418157.1142 | 430701.8277 | 443622.8825 | 456931.569 | 470639.516 | 484758.7015 | 499301.4626 | 514280.5065 | 529708.9216 | 545600.1893 | 561968.195 | 578827.2408 | 596192.058 | 614077.8198 | 632500.1544 | 651475.159 | 671019.4138 | 691149.9962 | 711884.4961 | 733241.031 | 755238.2619 | 777895.4098 | 801232.272 | 825269.2402 | 850027.3174 | 875528.1369 | 901793.981 | 928847.8005 | 956713.2345 | 985414.6315 | 1014977.0705 | 1045426.3826 | 1076789.1741 | 1109092.8493 | 1142365.6348 | 1176636.6038 | 1211935.7019 | 1248293.773 | 1285742.5862 | 1324314.8637 | 1364044.3097 | 1404965.6389 | 1447114.6081 | 1490528.0464 | 1535243.8878 | 1581301.2044 | 1628740.2405 | 1677602.4477 | 1727930.5212 | 1779768.4368 | 1833161.4899 | 1888156.3346 | 1944801.0246
Annual Pumping Cost (PSH)
| FPV Pumping Cost |  | 3395231.4558 | 92961432.0539 | 0 | 3395231.4558 | 3497088.3995 | 3602001.0515 | 3710061.083 | 3821362.9155 | 3936003.803 | 4054083.9171 | 4175706.4346 | 4300977.6276 | 4430006.9565 | 4562907.1652 | 4699794.3801 | 4840788.2115 | 4986011.8579 | 5135592.2136 | 5289659.98 | 5448349.7794 | 5611800.2728 | 5780154.281 | 5953558.9094 | 6132165.6767 | 6316130.647 | 6505614.5664 | 6700783.0034 | 6901806.4935 | 7108860.6883 | 7322126.5089 | 7541790.3042 | 7768044.0133 | 8001085.3337 | 8241117.8937 | 8488351.4306 | 8743001.9735 | 9005292.0327 | 9275450.7937 | 9553714.3175 | 9840325.747 | 10135535.5194 | 10439601.585 | 10752789.6325 | 11075373.3215 | 11407634.5212 | 11749863.5568 | 12102359.4635 | 12465430.2474 | 12839393.1548 | 13224574.9495 | 13621312.1979 | 14029951.5639 | 14450850.1108 | 14884375.6141 | 15330906.8825 | 15790834.089 | 16264559.1117 | 16752495.885 | 17255070.7616 | 17772722.8844 | 18305904.571 | 18855081.7081 | 19420734.1593
| Grid Off-Peak Cost |  | 1596875 | 43722435.0511 | 0 | 1596875 | 1644781.25 | 1694124.6875 | 1744948.4281 | 1797296.881 | 1851215.7874 | 1906752.261 | 1963954.8289 | 2022873.4737 | 2083559.6779 | 2146066.4683 | 2210448.4623 | 2276761.9162 | 2345064.7737 | 2415416.7169 | 2487879.2184 | 2562515.5949 | 2639391.0628 | 2718572.7947 | 2800129.9785 | 2884133.8779 | 2970657.8942 | 3059777.631 | 3151570.96 | 3246118.0888 | 3343501.6314 | 3443806.6804 | 3547120.8808 | 3653534.5072 | 3763140.5424 | 3876034.7587 | 3992315.8014 | 4112085.2755 | 4235447.8337 | 4362511.2688 | 4493386.6068 | 4628188.205 | 4767033.8512 | 4910044.8667 | 5057346.2127 | 5209066.5991 | 5365338.5971 | 5526298.755 | 5692087.7176 | 5862850.3492 | 6038735.8596 | 6219897.9354 | 6406494.8735 | 6598689.7197 | 6796650.4113 | 7000549.9236 | 7210566.4213 | 7426883.414 | 7649689.9164 | 7879180.6139 | 8115556.0323 | 8359022.7133 | 8609793.3947 | 8868087.1965 | 9134129.8124
| Total Cost (CAPEX+O&M+Grid Off-Peak) |  |  | 196993066.5836
136683867.105
| Net Cash Flow/ Annual Margin |  |  | -1501265.1985 | -51000000 | 1960593.5442 | 2011899.8695 | 2064527.777 | 2118510.61 | 2173882.5296 | 2230678.5337 | 2288934.4768 | 2348687.0902 | 2409974.0023 | 2472833.7597 | 2537305.8485 | 2603430.7165 | 2671249.7956 | 2740805.524 | 2812141.3706 | 2885301.858 | 2960332.5873 | 3037280.2628 | 3116192.7177 | 3197118.9398 | 3280109.0981 | 3365214.57 | 3452487.9687 | 3541983.1718 | 3633755.3497 | 3727860.9954 | 3824357.9542 | 3923305.4547 | 4024764.1398 | 4128796.0988 | 4235464.8998 | 4344835.6234 | 4456974.8961 | 4571950.925 | 4689833.5334 | 4810694.1967 | 4934606.079 | 5061644.0707 | 5191884.8265 | 5325406.805 | 5462290.3073 | 5602617.5188 | 5746472.5494 | 5893941.4762 | 6045112.3864 | 6200075.4207 | 6358922.8179 | 6521748.9605 | 6688650.421 | 6859726.0086 | 7035076.8174 | 7214806.2756 | 7399020.1947 | 7587826.8205 | 7781336.8846 | 7979663.6568 | 8182922.9989 | 8391233.4187 | 8604716.1256 | 8823495.0868
| Cumulative Cash Flow |  |  |  | -51000000 | -49039406.4558 | -47027506.5863 | -44962978.8094 | -42844468.1994 | -40670585.6698 | -38439907.1362 | -36150972.6593 | -33802285.5691 | -31392311.5668 | -28919477.8071 | -26382171.9586 | -23778741.2421 | -21107491.4465 | -18366685.9225 | -15554544.5519 | -12669242.6938 | -9708910.1065 | -6671629.8437 | -3555437.126 | -358318.1862 | 2921790.9119 | 6287005.4819 | 9739493.4506 | 13281476.6224 | 16915231.9722 | 20643092.9675 | 24467450.9217 | 28390756.3764 | 32415520.5162 | 36544316.6149 | 40779781.5148 | 45124617.1382 | 49581592.0343 | 54153542.9592 | 58843376.4926 | 63654070.6893 | 68588676.7683 | 73650320.8389 | 78842205.6655 | 84167612.4704 | 89629902.7778 | 95232520.2965 | 100978992.8459 | 106872934.3222 | 112918046.7086 | 119118122.1293 | 125477044.9472 | 131998793.9077 | 138687444.3287 | 145547170.3372 | 152582247.1546 | 159797053.4303 | 167196073.625 | 174783900.4455 | 182565237.3301 | 190544900.9869 | 198727823.9858 | 207119057.4045 | 215723773.5301 | 224547268.6169
| NPV |  |  | -1501265.1985 | bar: 0
| IRR |  |  | 4.836% | bar: 0
| Payback Period |  |  | 21.1336 | 0: Years
| LCOE (Before Pumping) |  |  | 0.10386 | 0: $/kWh
| LCOE (Pumping) |  |  | 0.33924 | 0: $/kWh
| Cost of Stored Energy (COSE) | Grid Off-Peak |  | 339.2354 | 0: $/MWh
Note on D14: Kerry Pep: Current Rate
Note on B32: Kerry Pep: According to IRENA Renewable Power Generation Cost Report 2021. Degradation of Wind Turbine is 0.5

## FPV Sensitivity
Economic analysis
Sensitivity analysis for FPV and PHS
FPV Sensitivity Results (60-Years)
Scenario 1 | Parameter (60yr base) | NPV (M$) | IRR (%) | LCOE($/kWh) | Comments / Comparison with 30yr case
Base case | As per FPV 60‑yr results | 22.05 | 5 | 0.15 | 30‑yr NPV = 10.56 M$, IRR = 4.5%
PPA +10% | PPA increased by 10% | 27.5 | 7 | 0.15 | 60‑yr NPV/IRR improve more than 30‑yr
PPA −10% | PPA decreased by 10% | 16.5 | 3 | 0.15 | 60‑yr more exposed to tariff reduction
CAPEX +20% | CAPEX increased by 20% | 24.9 | 4 | 0.17 | 30‑yr relatively more dominated by CAPEX
CAPEX −20% | CAPEX decreased by 20% | 19.1 | 6 | 0.13 | Both horizons benefit; 30‑yr strongly
OPEX +20% | Annual OPEX increased by 20% | 23.2 | 5 | 0.16 | 60‑yr more sensitive (longer O&M period)
OPEX −20% | Annual OPEX decreased by 20% | 20.9 | 4 | 0.14 | Bigger lifetime saving than 30‑yr
Energy yield +10% | Energy (MWh) increased by 10% | 22 | 5 | 0.14 | 60‑yr revenue uplift larger than 30‑yr
Energy yield −10% | Energy (MWh) decreased by 10% | 22 | 5 | 0.17 | 60‑yr revenue loss larger than 30‑yr
Discount rate = 5% | Lower discount rate (vs 6% base) | 28.2 | 3 | 0.14 | 60‑yr NPV rises more than 30‑yr
Discount rate = 7% | Higher discount rate (vs 6% base) | 17.7 | 6 | 0.16 | 60‑yr NPV falls more than 30‑yr
Discount rate = 9% | Much higher discount rate | 12.2 | 9 | 0.18 | Long‑life benefits heavily penalised

## PSH Sensitivity
Economic analysis
Sensitivity analysis for FPV and PHS
PHS sensitivity results (60-Years)
Scenario 1 | Parameter (60yr base) | NPV (M$) | IRR (%) | LCOE ($/kWh) | Comments / Comparison
Base NZ case | As per FPV 60‑yr results | 47.74 | 10% | 0.25 | Positive results in NPV and IRR
PPA +10% | PPA increased by 10% | 67.29 | 11% | 0.25 | Positive Improve in IRR & NPV
PPA −10% | PPA decreased by 10% | 28.19 | 8% | 0.25 | IRR & NPV drop but still viable
CAPEX +20% | CAPEX increased by 20% | 37.54 | 8% | 0.27 | Increasing CAPEX reduce IRR,NPV and increase LCOE
CAPEX −20% | CAPEX decreased by 20% | 57.94 | 12% | 0.24 | Reduced CAPEX increase IRR,NPV and decrease LCOE
OPEX +20% | Annual OPEX increased by 20% | 45.86 | 10% | 0.26 | Increasing OPEX reduce IRR,NPV and increase LCOE
OPEX −20% | Annual OPEX decreased by 20% | 49.6 | 10% | 0.25 | Reduced OPEX increase IRR,NPV and decrease LCOE
Energy yield +10% | Energy (MWh) increased by 10% | 58.54 | 11% | 0.25 | 60‑yr revenue uplift by large
Energy yield −10% | Energy (MWh) decreased by 10% | 36.93 | 9% | 0.27 | 60‑yr revenue reduced
Discount rate = 5% | Lower discount rate (vs 6% base) | 71.81 | 10% | 0.25 | 5% discount rate improves IRR,NPV and LCOE
Discount rate = 7% | Higher discount rate (vs 6% base) | 30.36 | 10% | 0.26 | 7% discount rate does not improves IRR,NPV and LCOE
Discount rate = 9% | Much higher discount rate | 7.8 | 10% | 0.27 | 9% discount rate does not improves IRR,NPV and LCOE
Pumping energy cost results
Scenario 1 | Pumping Price ($/MWh) | Spread vs 200 ($/MWh) | Pumping Energy Cost ($) | NPV (M$) | IRR (%) | LCOE ($/kWh) | Comment
Base NZ case | 70 | 130 | 87444870 | 47.74 | 10% | 0.25 | As per PSH base results
Haywards winter min | 67.37 | 132.63 | 84159441.41 | 51 | 10% | 0.25 | Slightly better than base
Haywards summer min | 0.72 | 199.28 | 899432.95 | 134.3 | 16% | 0.11 | Very strong arbitrage; major uplift in NPV/IRR
Higher off‑peak stress case | 100 | 100 | 124921243 | 10.26 | 6% | 0.32 | Reduced spread; weaker but still viable
Hayward seasonal and nodal price data
Hayward Seasonal |  | Nodal Price ($/MWh)
Season | Month | Min | Time | Max | Time | Average
Winter | Jun - Aug | 67.37 | 12pm-3pm | 234 | 6-8am & 6pm - 10pm | 140.27
Summer | Nov-Jan | 0.72 |  | 78.2 |  | 25.16