## Overview
Supplementary Material - Techno-Economic Feasibility of Underground Hydrogen Storage at Ahuroa with CCGT Integration
Hamna Habeebullah ¦ 300678091 ¦ Master of Renewable Energy ¦ Victoria University of Wellington ¦ Supervisor: AC Brent
All monetary values in NZD 2025 unless stated. USD converted at 1.70 NZD/USD. EUR converted at 1.85 NZD/EUR (Reserve Bank NZ May 2025).
Sheets | Content
S1_LCOH Assumptions | Input parameters for LCOH model from literature | LCOH Modelling
S2_Storage CAPEX | Storage conversion CAPEX for three scenarios
S3_Storage OPEX | Annual Storage Operating Costs
S4_Electrolyser Assumptions | Electrolyser equations and parameters
S5_Electrolyser CAPEX | Electrolyser CAPEX for three scenarios
S6_Electrolyser OPEX | Annual electrolyser operating costs
S7_LCOH Results | Full LCOH calculation and results
S8_Benchmark Comparison | LCOH compared against NZ and interanational benchmarks
S9_LCOH Sensitivity | One variable sensitivity tables for six parameters affecting the LCOH
S10_CCGT Assumptions | All equations and parameters for CCGT integration module | CCGT Integration
S11_CCGT Calculations | LCOE for Hydrogen and natural gas at TCC
S12_Cost Competitiveness | Cost gap and carbon price breakeven calculations
S13_CCGT sensitivity | Sensitivity of LCOE to gas price, retrofit, plant life, efficiency
S14_LCOH Charts | Charts for LCOH results and sensitivity | Charts and Chart Data
S15_CCGT Charts | Charts for LCOE and carbon price analysis
S16_Chart data LCOH | Data
S17_Chart data CCGT | Data
This workbook contains all the calculations for the research project. It is organised into two parts. The first part (from sheets 1 to 9) calculates how much it costs to produce and store green hydrogen at Ahuroa ,this is the LCOH model. The second part (sheets 10 to 13) takes that cost and works out how much it would cost to generate electricity using that hydrogen at the Taranaki Combined Cycle power station, this is the CCGT integration model. All calculations are done for three scenarios: conservative, base case, and optimistic. The conservative scenario assumes lower equipment reusability and current electrolyser costs, representing a worst-case outcome. The base case uses the actual injection rate measured from Ahuroa operational data as the main constraint on hydrogen production, with current electrolyser costs, this is the most realistic scenario. The optimistic scenario assumes the full theoretical reservoir capacity is used with projected 2030 electrolyser costs, representing the best-case outcome if infrastructure is upgraded and technology costs fall as expected.

## S1_LCOH Assumptions
Parameter | Value | Unit | Source | Page | Section | Notes
Reservoir Parameters
Reservoir Depth | 2000 | meters | J.Liu et al. 2025 | 9 | Section 2.4 Model Geometry | Tariki Sandstone Member ~2 km depth
Reservoir Temperature | 65 | degree celcius | J.Liu et al. 2025 | 2 | Table 1 | Original field measurement
Original reservoir pressure | 24 | MPa | J.Liu et al. 2025 | 2 | Table 1 | Initial hydrostatic pressure
Average prorosity | 14 | % | J.Liu et al. 2025 | 2 | Table 1 | History-matched; lab range 10.3–15.9%
Horizontal permeability | 40 | mD | J.Liu et al. 2025 | 2 | Table 1 | History-matched; lab range 15–102 mD
Vertical permeability | 4 | mD | J.Liu et al. 2025 | 2 | Table 1 | 10x anisotropy ratio
Gross reservoir thickness | 200 | meters | J.Liu et al. 2025 | 9 | Section 2.4 Model Geometry | Tariki Sandstone Member
Gas water contact depth | 2260 | meters | J.Liu et al. 2025 | 2 | Table 1 | From field measurements
Min operating pressure | 16 | MPa | J.Liu et al. 2025 | 11 | Section 2.6 Baseline simulation | Current permitted minimum
Max operating pressure | 24 | MPa | J.Liu et al. 2025 | 11 | Section 2.6 Baseline simulation | Must not exceed original pressure
Storage Capacity
Cushion gas volume | 6000 | TJ | Ahuroastorage.xlx | All rows | CUSHION_GAS_TJ | Consistent across 2,246 daily records
Cushion gas volume (Converted) | 1.667 | TWh | 6000*0.2778 | Calculation | Calculation | Own calculation
Working gas - Conservative | 0.45 | TWh H2 | Contact energy 2022,Higgs et al.2024 |  |  | Current water-affected effective capacity
Working gas - Base | 0.6 | TWh H2 | Contact energy 2022,Higgs et al.2024 |  |  | Partial remediation assumed
Working gas - Optimistic | 1.4 | TWh H2 | Higgs et al.2024 | 14 | Table 6 | Full theoretical capacity if remediated
H2 Energy density LHV | 33.3 | kWh/kg | Standard Thermodynamic Value | - | - | Lower Heating Value
M_H2 Conservative | 13513513.5135 | kg/year | Working gas*10^9/H2 Energy density | kg=kWh/(kWh/kg) | - | -
M_H2 Base | 18018018.018 | kg/year | Working gas*10^9/H2 Energy density | kg=kWh/(kWh/kg) | - | -
M_H2 Optimistic | 42042042.042 | kg/year | Working gas*10^9/H2 Energy density | kg=kWh/(kWh/kg) | - | -
H2 Withdrawal efficiency | 90 | % | J.Liu et al.2025 | 17 | Section 3.5 | Range 89–92.3% from Ahuroa simulations; 90% conservative
H2 Loss rate (Diffussion) | 1 | % | Pan et al. 2021 | 6 | Diffussion losses | 1% H2 loss over 15 years in high-porosity reservoirs
Cycling Frequency | 2 | cycles per year | Ahuroastorage.xlx | All rows | Derived from Seasonal injection/withdrawal pattern | Seasonal storage - winter inject, summer/autumn withdraw
Natural gas to H2 Conversion Factor | 0.27 | - | Higgs et al.2024 | 14 | Table 6 footnote | Energy conversion ratio used to derive H2 equivalent capacity
Financial Parameters
Project Lifetime (n) | 30 | years | lord et al.2014 | 6 | Table 2 | Industry standard for underground storage infrastructure
Discount rate (i) | 0.08 | - | New Zealand Treasury Circular 2024/15. Yousefi et al.2023 uses discount rates in the range of 5-10% for UHS economic modelling for a European depleted reservoir. | 2 | Table of discount rates | SOC rate applies as project has mainly commercial costs and benefits. SRTP rate of 2% used as mandatory sensitivity test per Treasury guidance.
CRF | 0.088827 | - | Calculated from discount rate and lifetime | CRF = [i × (1 + i)^n] / [(1 + i)^n − 1] | Standard financial formula | -
USD to NZD exchange rate | 1.7 | - | Current market rate as per May 2025 | - | Reserve Bank of NZ | -
Tax rate | 28 | % | New Zealand Inland Revenue Website | nzird.gov.nz |  | NZ resident company rate. NOTE: Deng et al. uses 15% (China)
Contigency fund rate | 12 | % | Deng et al.2025 | 17 | Table 2 Section 5 | Applied to total construction costs
Equipment lifetime | 30 | years | lord et al.2014 | 6 | Table 2 | -
Capex Parameters
Well maintanance-horizontal (CUGS) | 0.62 | $M/well | Deng et al.2025 | 16 | Table 2 Section 2.3 | 2 horizontal wells; existing wells maintained not replaced
Well maintanance-straight (CUGS) | 0.49 | $M/well | Deng et al.2025 | 16 | Table 2 Section 2.3 | 2 straight wells
Production equipment (both routes) | 0.35 | $M/well | Deng et al.2025 | 16 | Table 2 Section 2.2 | Required regardless of CUGS or CDGR route
Gas transmission pipeline maintanance (CUGS) | 6.51 | $M/set | Deng et al.2025 | 16 | Table 2 Section 2.5 | Existing pipeline refurbished for H2 compatibility
Equipment maintanance (CUGS) | 1.68 | $M/set | Deng et al.2025 | 16 | Table 2 Section 2.5 | H2 embrittlement-resistant component replacements
Cushion gas CO2 (Base) | 90000 | $/MCM | Deng et al.2025 | 16 | Table 2 Section 3.1 | Per million cubic metres of cushion gas
Cushion gas N2 (Alternative) | 50000 | $/MCM | Deng et al.2025 | 16 | Table 2 Section 3.1 | N2 cheaper but less effective than CO2
Cushion gas injection fee | 23815 | $/MCM | Deng et al.2025 | 16 | Table 2 Section 3.2 | Energy and labour costs for large-scale injection
Existing asset value - wells (CUGS) | 60 | % of original | Deng et al.2025 | 16 | Table 2 Section 4 | Residual value of existing high-quality production wells
Existing asset value surface equipment (CUGS) | 60 | % of original | Deng et al.2025 | 16 | Table 2 Section 4 | Residual value of compressors and surface facilities
Total Capex CUGS route (base/optimistic) | 52-55 | $M USD | Deng et al.2025 | 16 | Table 2 | -
Total Capex CDGR route (conservative) | 83-86 | $M USD | Deng et al.2025 | 16 | Table 2 | New wells + all surface infrastructure
Cushion gas volume for cost calculation | 170 | MCM | Calculated: 6000 TJ × 0.02832 MCM/TJ | Conversion: 1 TJ = 0.02832 MCM | ≈ 169.9 MCM rounded to 170 | ≈ 169.9 MCM rounded to 170
Cushion gas as % of total investment | 50 | % | lord et al.2014 | 3 | Depleted reservoirs section | Industry benchmark; confirmed by Deng et al. (2025)
Compressor cost per unit 1800 kW | 3.2 | $M USD | Deng et al.2025 | 16 | Table 2 Section 2.4 | Already installed at Ahuroa — $0 CUGS route (key advantage)
OPEX Parameters
Gas injection expenses | 4.43 | $M/year | Deng et al.2025 | 17 | Table 3 Section 1.1 | Largest OPEX item — energy and labour for injection
Labour Cost (20 staff)-NZ adjusted | 0.76 | $M/year | Deng et al.2025 (Adjusted for NZ) | 17 | Table 3 | Deng: $38k/person; NZ engineering salary ~NZD 100k/person × 20
Fuel costs | 0.37 | $M/year | Deng et al.2025 | 17 | Table 3 Section 1.2 | -
Monitoring well and operations | 0.44 | $M/year | Deng et al.2025 | 17 | Table 3 Section 1.2 | Monitoring wells + well management combined
Management fees | 2.16 | $M/year | Deng et al.2025 | 17 | Table 3 Section 2.1 | Safety production + other management
Financial and sales expenses | 1.4 | $M/year | Deng et al.2025 | 17 | Table 3 Section 2.2 | -
Equipment depreciation | 0.56 | $M/year | Deng et al.2025 | 17 | Table 3 Section 1.3 | -
Energy parameters & LCOH formula parameters
Compression Energy | 2.2 | kWh/kg H2 | Lord et al.2014 | 6 | Table 2 | Physical/thermodynamic parameter - stable across contexts
New Zealand Electricity Price (Base) | 100 | NZD/MWh | EMI Marketing statistics+MBIE hydrogen eonomic modelling report 2023 | 48 | Figure 40 | Representative long-run average wholesale price. NOT retail tariff.
New Zealand Electricity Price (Low) - Sensitivity | 70 | NZD/MWh | EMI Marketing statistics+MBIE hydrogen eonomic modelling report 2024 | 48 | Figure 40 | Low renewable/PPA scenario
New Zealand Electricity Price (High) - Sensitivity | 150 | NZD/MWh | EMI Marketing statistics+MBIE hydrogen eonomic modelling report 2025 | 48 | Figure 40 | High-price market scenario
New Zealand Electricity Price (Stress) - Sensitivity | 250 | NZD/MWh | EMI Electricity Authority Wholesale Marketing Data | emi.ea.govt.nz/wholesale/Reports/w_p_c | - | Winter/dry-year stress scenario - sensitivity only
Electricity Price in NZD/kWh (Base) | 0.1 | NZD/kWh | Calculated | - | - | -
Electrolyser Efficiency | 66 | % of LHV | IEA GHR 2024 | 3 | - | -
Benchmarking & Revenue Assumptions
New Zealand green H2 cost - near term | 6 to 10 | NZD/kg | MBIE NZ Hydrogen Scenarios Report (Sept 2022) | 41 | Figure 5.2 | Lowest levelised cost of H2 produced in NZ
New Zealand green H2 cost - long term (2050) | 2.87 to 3.73 | NZD/kg | MBIE NZ Hydrogen Scenarios Report (Sept 2022) | 41 | Figure 5.2 | Projected long-term competitive cost
EECA Current H2 indiative price | 8 | NZD/kg | EECA Hydrogen Reference | eeca.govt.nz/insights/energy/renewable-energy/hydrogen/ |  | Current NZ green hydrogen benchmark
EECA Long term H2 Target | 2 | NZD/kg | EECA Hydrogen Reference | eeca.govt.nz/insights/energy/renewable-energy/hydrogen/ |  | Long-term competitive target for NZ

## S2_Storage CAPEX
CAPEX Calculations of Ahuroa UHS Facility (CUGS Route)
All USD values converted to NZD using exchange rate in Assumptions sheet (1.70). Scale: Deng et al. model based on 100 MCM; Ahuroa ≈ 90 MCM, scale factor 0.30 applied.
Base Case CAPEX estimation for conversion
Cost Item | USD Amount ($M) | NZD Amount ($M) (=Value*1.7 exchange rate) | Qty | Total NZD ($M) | Notes | Source
1. WELL COSTS
Well - horizontal | 0.62 | 1.054 | 2 | 2.108 | 2 horizontal wells; existing wells maintained not replaced | Deng et al. 2025 ¦ Page 16 ¦ Table 2 ¦ Section 2.3
Well - straight | 0.49 | 0.833 | 2 | 1.666 | 2 straight wells | Deng et al. 2025 ¦ Page 16 ¦ Table 2 ¦ Section 2.3
Production equipment | 0.35 | 0.595 | 4 | 2.38 | Required for both CUGS and CDGR routes | Deng et al. 2025 ¦ Page 16 ¦ Table 2 ¦ Section 2.2
2. SURFACE FACILITY COSTS
Gas transmission pipeline maintenance | 6.51 | 11.067 | 1 | 11.067 | Existing pipeline refurbished for H2 compatibility | Deng et al. 2025 ¦ Page 16 ¦ Table 2 ¦ Section 2.5
Equipment maintenance and H2 upgrades | 1.68 | 2.856 | 1 | 2.856 | H2 embrittlement-resistant component replacements | Deng et al. 2025 ¦ Page 16 ¦ Table 2 ¦ Section 2.5
3. CUSHION GAS COSTS (170 MCM = 6,000 TJ converted)
Cushion gas - CO2 (base case) | 15.3 | 26.01 | 1 | 26.01 | 90,000 $/MCM × 170 MCM = $15.3M USD | Deng et al. 2025 ¦ Page 16 ¦ Table 2 ¦ Section 3.1
Cushion gas injection fee | 4.0485 | 6.8825 | 1 | 6.8825 | 23,815 $/MCM × 170 MCM = $4.05M USD | Deng et al. 2025 ¦ Page 16 ¦ Table 2 ¦ Section 3.2
4. CONTINGENCY FUND (12% of construction costs)
Construction contingency fund (12%) | 3.4798 | 5.9157 | 1 | 5.9157 | 12% of total pre-contingency costs | Deng et al. 2025 ¦ Page 16 ¦ Table 2 ¦ Section 5
TOTAL CAPEX (NZD $M) | 58.8852
TOTAL CAPEX (NZD full $) | 58885239.2 | ← This value feeds into LCOH sheet
Note:
Deng et.al. 2025 suggests 60% of equipment reusability in base case scenario. Taking this information into consideration, three scenarios are identified for sensitivity analysis
in CAPEX calculations. The base case scenario have 60% equipment reusability. The conservative scenario have a 15% equipment reusability.
Equipment reusability percentage is not taken in the range 0-10% for conservative scenario because Ahuroa field is functional and is not a depleted reservoir now.
Optimistic scenario is about 70% equipment reusability which is a best case imaginary scenario.
7. Residual Value Credit
Existing wells | 15.5 | 26.35 | 1 | 26.35 | 60% of Residual advantage of existing well assets | Deng et al. 2025 ¦ Page 16 ¦ Table 2 ¦ Section 4
Surface equipments | 14.06 | 23.902 | 1 | 23.902 | 60% of Residual advantage of existing well assets | Deng et al. 2025 ¦ Page 16 ¦ Table 2 ¦ Section 4
Total residual value credit (in $M NZD) | 50.252 |  |  |  | 60% of Residual advantage of existing well assets | Deng et al. 2025 ¦ Page 16 ¦ Table 2 ¦ Section 4
SCENARIO CAPEX COMPARISON - Conservative (CDGR), Base (CUGS Calc) & Optimistic (CUGS Low)
Scenario | Percentage of equipment reusability | Residual credit advantage | CAPEX $M NZD (gross) | CAPEX $M NZD (net) (=CAPEXgross-Residual credit advantage)
CONSERVATIVE | 15 | -22.6134 | 58.8852 | 81.4986
BASE CASE | 60 | 0 | 58.8852 | 58.8852
OPTIMISTIC | 70 | 5.0252 | 58.8852 | 53.86

## S3_Storage OPEX
Annual OPEX Calculations for Ahuroa UHS facility
1. OPEX Economic normalisation values for New Zealand context (last updated on 15 May,2025)
Parameter | Value | Unit | Source | Note
New Zealand Labour Cost | 100000 | NZD/year | https://tahatu.govt.nz/work/explore-career-ideas/118-energy-and-chemicals | Average value for labour in Energy and Chemicals
Deng et al. 2025 injection volume | 300 | MCM/year | Deng et al 2025
Ahuroa injection volume as per operational data 2020-23 | 90 | MCM/year | Ahuroastorage.xlx
Volume scaling factor | 0.3
New Zealand Wholesale Electricity Price | 100 | NZD/MWh | EMI Marketing statistics+MBIE hydrogen eonomic modelling report 2023 | Representative long-run average wholesale price. NOT retail tariff.
2. Calculated OPEX Values
Cost Item | USD/year ($M) | NZD/year ($M) | Notes | Source
a. PRODUCTION COSTS
Gas injection expenses | 4.43 | 2.2593 | Largest OPEX item — energy and labour for H2 injection | Deng et al. 2025 ¦ Page 17 ¦ Table 3 ¦ Section 1.1
b. UHS FACILITY OPERATION
Labour - 20 staff (NZ adjusted) | 0.76 | 2 | NZ adjustment: Deng uses $38k/person (China); NZ ~$100k/person. NZD value = 20 × $100,000 = $2.0M NZD | Deng et al. 2025 Table 3 — NZ salary adjustment applied
Fuel costs | 0.37 | 0.629 | Operational fuel for facility | Deng et al. 2025 ¦ Page 17 ¦ Table 3 ¦ Section 1.2
Electricity (monitoring/pumps) | 0.04 | 0.068 | Negligibly small conversion changes | Deng et al. 2025 ¦ Page 17 ¦ Table 3 ¦ Section 1.2
Materials | 0.05 | 0.085 | Consumables and materials | Deng et al. 2025 ¦ Page 17 ¦ Table 3 ¦ Section 1.2
Monitoring | 0.16 | 0.272 | Reservoir and facility monitoring | Deng et al. 2025 ¦ Page 17 ¦ Table 3 ¦ Section 1.2
Wells operations | 0.28 | 0.476 | Well management and operations | Deng et al. 2025 ¦ Page 17 ¦ Table 3 ¦ Section 1.2
Wells management | 0.11 | 0.187 | Administrative well management | Deng et al. 2025 ¦ Page 17 ¦ Table 3 ¦ Section 1.2
Maintenance and repair | 0.05 | 0.085 | Routine maintenance | Deng et al. 2025 ¦ Page 17 ¦ Table 3 ¦ Section 1.2
Other operating costs | 0.15 | 0.255 | Miscellaneous operational costs | Deng et al. 2025 ¦ Page 17 ¦ Table 3 ¦ Section 1.2
c. DEPRECIATION AND AMORTISATION
Equipment depreciation | 0.56 | 0.952 | Annual depreciation of equipment assets | Deng et al. 2025 ¦ Page 17 ¦ Table 3 ¦ Section 1.3
d. INDIRECT EXPENSES
Safety production management | 1.62 | 2.754 | Safety and compliance management | Deng et al. 2025 ¦ Page 17 ¦ Table 3 ¦ Section 2.1
Other management fees | 0.54 | 0.918 | General management overhead | Deng et al. 2025 ¦ Page 17 ¦ Table 3 ¦ Section 2.1
Sales expenses | 0.72 | 1.224 | Commercial and sales costs | Deng et al. 2025 ¦ Page 17 ¦ Table 3 ¦ Section 2.2
Financial expenses | 0.68 | 1.156 | Banking and financial charges | Deng et al. 2025 ¦ Page 17 ¦ Table 3 ¦ Section 2.2
Total OPEX | 13.3203 | $M NZD/year

## S4_Electrolyser Assumptions
Assumptions and Equations used for electrolyser cost calculations.
1. Equations
Equation | Formula | Variables | Result Unit | Type | Source
EQ-1 Annual energy required | Energy (kWh/yr) = M_H2 × LHV ÷ η | M_H2 = annual H2 output (kg/yr) LHV = 33.3 kWh/kg η = electrolyser efficiency (0.66) | kWh/yr | Standard energy balance (first law of thermodynamics) | Standard engineering equation
EQ-2 Electrolyser capacity | Capacity (kW) = Energy (kWh/yr) ÷ Operating hours (hrs/yr) | Energy from EQ-1 Operating hours = hrs/yr the electrolyser runs | kW | Standard power-energy-time Power = Energy ÷ Time | Standard engineering equation
EQ-3 Unit conversion kW to MW | Capacity (MW) = Capacity (kW) ÷ 1,000 | kW from EQ-2 | MW | SI unit conversion | Standard SI conversion
EQ-4 CAPEX in USD | CAPEX (USD $M) = Capacity (kW) × Rate (USD/kWe) ÷ 1,000,000 | kW from EQ-2 Rate (USD/kWe) from IEA GHR 2024 p.3 | USD $M | Engineering economics cost estimation | IEA (2024) GHR Assumptions Annex p.3
EQ-5 CAPEX in NZD | CAPEX (NZD $M) = CAPEX (USD $M) × Exchange rate | USD $M from EQ-4 Exchange rate = 1.70 NZD/USD | NZD $M | Currency conversion | Reserve Bank of New Zealand - May 2025
EQ-6 Injection-constrained M_H2 | M_H2 (kg/yr) = Injection rate (MCM/day) × Injection days × H2 density (kg/MCM) | Injection rate from AhuroaStorage.xlsx Injection days from AhuroaStorage.xlsx H2 density = 89,900 kg/MCM | kg/yr | Derived - site-specific from operational data | AhuroaStorage.xlsx (2020–2023) + NIST standard H2 density
EQ-7 H2 density per MCM | kg/MCM = H2 density (kg/m³) × 1,000,000 (m³/MCM) | H2 density = 0.0899 kg/m³ at STP (0°C, 1 atm) 1 MCM = 1,000,000 m³ | kg/MCM | Physical constant + unit conversion | NIST Chemistry WebBook H2 molecular weight 2.016 g/mol
EQ-8 OPEX maintenance | OPEX maintenance (NZD $M/yr) = CAPEX (NZD $M) × 0.03 | CAPEX from EQ-5 3% annual OPEX rate from IEA GHR 2024 p.3 (includes stack replacement) | NZD $M/yr | IEA standard rate applied to CAPEX | IEA (2024) GHR Assumptions Annex p.3 ¦ Row: Annual OPEX = 3%
EQ-9 OPEX electricity | OPEX elec (NZD $M/yr) = M_H2 × LHV ÷ η × P_elec ÷ 1,000,000 | M_H2 (kg/yr) from EQ-6 or working gas LHV = 33.3 kWh/kg η = 0.66 P_elec = 0.10 NZD/kWh (= 100 NZD/MWh) | NZD $M/yr | EQ-1 applied with NZ price (dominant cost item) | NZ electricity: MBIE Hydrogen Economic Modelling Report Dec 2023, p.48 Fig 40
EQ-10 Total OPEX | Total OPEX (NZD $M/yr) = OPEX maintenance + OPEX electricity | From EQ-8 and EQ-9 | NZD $M/yr | Simple summation | Derived from EQ-8 and EQ-9
EQ-11 Stack replacements | Replacements = Project life (yrs) × Operating hours (hrs/yr) ÷ Stack lifetime (hrs) | Project life = 30 years Operating hours = 8,760 hrs/yr Stack lifetime = 50,000 hrs | count (number) | Informational only (cost in 3% OPEX rate) | IEA GHR 2024 p.3 - stack lifetime Lord et al. (2014) - project life
2. Assumptions - From IEA (2024)
Parameter | 2023 Value (Current) | NZE 2030 (Projection) | Unit | Source | Page / Table / Row | Notes
Electrolyser system CAPEX - global average | 2160 | 960 | USD/kWe | IEA (2024). Global Hydrogen Review 2024: Assumptions Annex. International Energy Agency, Paris. CC BY 4.0. URL: https://iea.blob.core.windows.net/assets/36017d2f-747b-4993-b06d-33209fe143fa/GHR24AssumptionsAnnex.pdf | p.3 ¦ Table: 'Production pathways — Hydrogen (Water electrolysis)' ¦ Row: 'CAPEX* (global average)' | 2023 value used for conservative and base case. NZE 2030 used for optimistic sensitivity only. IEA notes only 4% of announced pipeline has reached FID as of 2024.
Electrolyser system CAPEX - China (reference only) | 1100 | 620 | USD/kWe | IEA (2024). Global Hydrogen Review 2024: Assumptions Annex. International Energy Agency, Paris. CC BY 4.0. URL: https://iea.blob.core.windows.net/assets/36017d2f-747b-4993-b06d-33209fe143fa/GHR24AssumptionsAnnex.pdf | p.3 ¦ Table: 'Production pathways — Hydrogen' ¦ Row: 'CAPEX* (China)' | Listed for reference only. NOT used in Ahuroa model
Efficiency (LHV) | 66 | 69 | % LHV | IEA (2024). Global Hydrogen Review 2024: Assumptions Annex. International Energy Agency, Paris. CC BY 4.0. URL: https://iea.blob.core.windows.net/assets/36017d2f-747b-4993-b06d-33209fe143fa/GHR24AssumptionsAnnex.pdf | p.3 ¦ Table: 'Production pathways — Hydrogen' ¦ Row: 'Efficiency (LHV)' | LHV = Lower Heating Value basis, 66% used.
Annual OPEX | 3% | 3% | % of CAPEX per year | IEA (2024). Global Hydrogen Review 2024: Assumptions Annex. International Energy Agency, Paris. CC BY 4.0. URL: https://iea.blob.core.windows.net/assets/36017d2f-747b-4993-b06d-33209fe143fa/GHR24AssumptionsAnnex.pdf | p.3 ¦ Table: 'Production pathways — Hydrogen' ¦ Row: 'Annual OPEX' | Includes stack replacement cost implicitly. Do NOT add separate stack replacement cost on top of this.
Stack lifetime - optimum economic value | 50000 | 50000 | operating hours | IEA (2024). Global Hydrogen Review 2024: Assumptions Annex. International Energy Agency, Paris. CC BY 4.0. URL: https://iea.blob.core.windows.net/assets/36017d2f-747b-4993-b06d-33209fe143fa/GHR24AssumptionsAnnex.pdf | p.3 ¦ Table: 'Production pathways — Hydrogen' ¦ Row: 'Stack lifetime (operating hours)**' | At 8,760 hrs/yr: 50,000 ÷ 8,760 = 5.7 yrs per stack. Over 30-yr project = ~5 replacements.
3. AHUROA OPERATIONAL PARAMETERS FROM AhuroaStorage.xlsx
Parameter | Value | Unit | Source | Derivation | Notes
Average daily injection rate | 0.6 | MCM/day | AhuroaStorage.xlsx - daily operational data 2020–2023 | Average of positive CHANGE_IN_STORAGE_TJ values ÷ 35.8 TJ/MCM = 21.6 TJ/day ÷ 35.8 = 0.60 MCM/day | Natural gas injection rate. Used as physical flow rate proxy for H2 - same infrastructure, same MCM/day.
Annual injection days | 196 | days/yr | AhuroaStorage.xlsx - daily operational data 2020–2023 | Count of days with positive CHANGE_IN_STORAGE_TJ across 2020–2023. Total 1,176 injection days ÷ 6 years = 196 days/yr. | Seasonal pattern: inject April–October. Withdrawal: November–March.
H2 density at standard conditions | 0.0899 | kg/m³ | NIST Chemistry WebBook - National Institute of Standards and Technology | H2 molecular weight = 2.016 g/mol. At STP (0°C, 1 atm): density = 0.0899 kg/m³. Standard physical constant. | Used in EQ-7 to convert MCM (volume) to kg (mass).
H2 density per MCM (EQ-7) | 89900 | kg/MCM | Calculated - EQ-7 | EQ-7: 0.0899 kg/m³ × 1,000,000 m³/MCM = 89,900 kg/MCM | Converts Ahuroa injection volume in MCM to mass of H2 in kg.
Annual injectable H2 - BASE CASE (EQ-6) | 10572240 | kg/yr | Calculated - EQ-6 ¦ AhuroaStorage.xlsx + NIST | EQ-6: 0.60 MCM/day × 196 days × 89,900 kg/MCM = 10,572,240 kg/yr = 0.352 TWh H2 | PRIMARY BASE CASE. Injection rate is binding constraint - not working gas volume. Sizing electrolyser above this rate wastes capital.
M_H2 - CONSERVATIVE (working gas basis)(theoretical value assumed for electrolyser sizing) | 13513514 | kg/yr | Working gas 1.40 TWh ÷ LHV 33.3 kWh/kg × 1,000,000 | 0.45 × 10⁹ Wh ÷ 33.3 Wh/g = 13,513,514 kg | Contact Energy (2022). Used for conservative sensitivity case only.
M_H2 - OPTIMISTIC (working gas basis) | 42042042 | kg/yr | Working gas 1.40 TWh ÷ LHV 33.3 kWh/kg × 1,000,000 | 1.40 × 10⁹ Wh ÷ 33.3 Wh/g = 42,042,042 kg | Higgs et al. (2024) Table 6 p.14. Used for optimistic sensitivity case only.
4. Other parameters used in calculations
Parameter | Value | Unit | Source | Page / Section | Notes
H2 LHV | 33.3 | kWh/kg | Standard thermodynamic constant | IEA/IRENA standard | Lower Heating Value. Used in EQ-1, EQ-6, EQ-9.
Electrolyser efficiency (eta) | 0.66 | decimal (66%) | IEA (2024) GHR Assumptions Annex | p.3 ¦ Row: Efficiency (LHV) ¦ 2023 value | Convert to decimal for EQ-1: 66% ÷ 100 = 0.66
USD to NZD exchange rate | 1.7 | NZD/USD | Reserve Bank of New Zealand | May 2025 current market rate | Used in EQ-5.
NZ wholesale electricity price | 100 | NZD/MWh | MBIE Hydrogen Economic Modelling Report Dec 2023 | p.48 ¦ Figure 40 | See Assumptions 1 sheet
Project lifetime | 30 | years | Lord et al. (2014). Deng et al. (2025). | Lord: p.6 Table 2 ¦ Deng: p.17 S4.3 | Electrolyser plant lifetime assumed equal to project lifetime. IEA does not state electrolysis lifetime.
Operating hours per year - base case | 8760 | hrs/yr | Own assumption | Grid-connected electricity basis | Electrolyser runs continuously on grid power = 365 × 24 = 8,760 hrs/yr.
H2 withdrawal efficiency | 90 | % | Liu et al. (2025) | p.17 ¦ Section 3.5 | Applied to M_H2 in LCOH: M_H2_effective = M_H2 × 0.90
H2 diffusion loss rate | 1 | %/yr | Pan et al. (2021) | p.6 ¦ Diffusion losses | Applied to M_H2: M_H2_net = M_H2_eff × 0.99
Note: Water costs excluded from IEA(2024) cost analysis

## S5_Electrolyser CAPEX
ELECTROLYSER CAPEX CALCULATIONS - Ahuroa UHS Facility
Conservative/Base case = injection-rate constrained from AhuroaStorage.xlsx. Optimistic = working gas scenarios. All equations referenced to Electrolyser Assumptions sheet Section 1.
Calculation Step | Equation Used (see Assumptions S1) | CONSERVATIVE | BASE CASE | OPTIMISTIC | Unit
STEP 0 - SCENARIO DEFINITIONS
M_H2 used in each scenario | See Assumptions Sheet Section 3 | 13513514 | 10572240 | 42042042 | kg/yr
CAPEX rate used | IEA GHR 2024 p.3 | 2160 | 2160 | 960 | USD/kWe
Operating hours per year | See Assumptions S4 | 8760 | 8760 | 8760 | hrs/yr
STEP 1 - Annual energy required by electrolyser (EQ-1)
Annual energy required | EQ-1: Energy = M_H2 × LHV ÷ η = M_H2 × 33.3 kWh/kg ÷ 0.66 | 681818206.3636 | 533417563.6364 | 2121212119.0909 | kWh/yr
Same - converted to MWh/yr |  | 681818.2064 | 533417.5636 | 2121212.1191 | MWh/yr
STEP 2 - Required electrolyser capacity (EQ-2 and EQ-3)
Capacity (kW) | EQ-2: Capacity (kW) = Energy (kWh/yr) ÷ Operating hours (hrs/yr) | 77833.1286 | 60892.4159 | 242147.5022 | kW
Capacity (MW) | EQ-3: Capacity (MW) = Capacity (kW) ÷ 1,000 | 77.8331 | 60.8924 | 242.1475 | MW
STEP 3 - Electrolyser CAPEX in USD (EQ-4)
CAPEX (USD $M) | EQ-4: CAPEX (USD $M) = Capacity (kW) × Rate (USD/kWe) ÷ 1,000,000 | 168.1196 | 131.5276 | 232.4616 | USD $M
STEP 4 - Electrolyser CAPEX in NZD — FINAL RESULT (EQ-5)
CAPEX (NZD $M) ← FINAL CAPEX RESULT | EQ-5: CAPEX (NZD $M) = CAPEX (USD $M) × 1.70 | 285.8032 | 223.597 | 395.1847 | NZD $M

## S6_Electrolyser OPEX
ELECTROLYSER OPEX CALCULATIONS - Annual Operating Costs for Ahuroa UHS
All equations from Assumptions Sheet Section 1.
OPEX Component | Equation Used (see Assumptions S1) | CONSERVATIVE | BASE CASE | OPTIMISTIC | Unit | Source / Notes
OPEX PART 1 - Maintenance and Stack Replacement (EQ-8: 3% of CAPEX per year)
IEA GHR 2024 p.3 - Annual OPEX row = 3% of CAPEX per year.
Stack replacements over 30 years | EQ-11: 30 × hrs/yr ÷ 50,000 | 5.256 | 5.256 | 5.256 | number | Informational only - cost captured in 3% maintenance rate Base: 30 × 8,760 ÷ 50,000 = 5.3 replacements IEA GHR 2024 p.3 footnote **: stack lifetime 50,000 hrs
Annual maintenance OPEX (NZD $M/yr) | EQ-8: OPEX maint = CAPEX (NZD $M) × 0.03 | 8.5741 | 6.7079 | 11.8555 | NZD $M/yr | Con: 285.80 × 0.03 = NZD 8.574M/yr Base: 223.60 × 0.03 = NZD 6.708M/yr Opt: 395.18 × 0.03 = NZD 11.855M/yr IEA (2024) GHR Assumptions Annex p.3 ¦ Row: Annual OPEX = 3%
OPEX PART 2 - Electrolyser Electricity Cost (EQ-9: dominant cost)
EQ-9: C_elec = M_H2 × LHV ÷ η × 0.10 NZD/kWh ÷ 1,000,000
Annual electricity cost (NZD $M/yr) | EQ-9: C_elec = M_H2 × LHV ÷ η × 0.10 ÷ 1,000,000 = EQ-1 result × 0.10 ÷ 1,000,000 | 68.1818 | 53.3418 | 212.1212 | NZD $M/yr | P_elec = NZD 0.10/kWh = 100 NZD/MWh Source: MBIE Hydrogen Economic Modelling Report Dec 2023 p.48 Fig 40 Con: 681,818,182 kWh × 0.10 ÷ 1,000,000 = NZD 68.182M/yr Base: 533,417,564 kWh × 0.10 ÷ 1,000,000 = NZD 53.342M/yr Opt: 2,121,212,121 kWh × 0.10 ÷ 1,000,000 = NZD 212.121M/yr
TOTAL ANNUAL ELECTROLYSER OPEX (EQ-10: maintenance + electricity)
| Equation | Conservative | Base Case | Optimistic | Unit | Notes
TOTAL ELECTROLYSER OPEX (NZD $M/yr) | EQ-10: Maint + Electricity | 76.7559 | 60.0497 | 223.9768 | NZD $M/yr | Feeds into LCOH numerator. Add to storage OPEX (NZD 13.3M/yr).

## S7_LCOH results
LCOH Calculation
Formula | LCOH = (CAPEX_storage × CRF + CAPEX_electrolyser × CRF + OPEX_storage + OPEX_electrolyser + C_energy) ÷ M_H2_effective,Where: M_H2_effective = M_H2 × withdrawal efficiency × (1 − loss rate) C_energy = M_H2_effective × compression energy × electricity price | Standard LCOH modelling structure. Lord et al.2014 Page 6. Reference in Yousefi et al. 2023 Page 28828.
Parameter | CONSERVATIVE | BASE Case Values | Optimistic | Unit | Notes
CAPEX (NZD $M) (Storage+Production) | 367.3019 | 282.4822 | 449.0448 | $M NZD | Linked from CAPEX sheets
CAPEX (NZD $M) (Storage only) | 81.4986 | 58.8852 | 53.86 | $M NZD | Linked from CAPEX Storage sheet
Capital Recovery Factor (CRF) | 0.088827 | 0.088827 | 0.088827 | - | From Assumptions sheet
OPEX (NZD $M/year) (Storage+Production) | 90.0762 | 73.37 | 237.2971 | $M NZD/year | Linked from OPEX sheets
OPEX (NZD $M/year) (Storage only) | 13.3203 | 13.3203 | 13.3203 | $M NZD/year | Linked from OPEX production sheet
Compression energy | 2.2 | 2.2 | 2.2 | kWh/kg H2 | From Assumptions - Lord et al. 2014, Page 6 Table 2
Electricity price (base case) | 100 | 100 | 100 | NZD/MWh | Representative wholesale price - MBIE Dec 2023 Page 48 Fig 40
Electricity price (base case) | 0.1 | 0.1 | 0.1 | NZD/KWh | MWh to KWh conversion
Annual H2 output according to for ahuroa injection data | 10572240 | 10572240 | 42042042 | kg/year | From Electrolyser Assumptions, except conservative case where LCOH is calculated with actual value from ahuroa
Withdrawal efficiency adjustment | 0.9 | 0.9 | 0.9 |  | 90% from Liu et al. 2025 - applied to M_H2 as multiplier
Hydrogen diffussion loss rate | 0.01 | 0.01 | 0.01 |  | 1% from Pan et al.2021 page 6
M_H2_Effective | 9419865.84 | 9419865.84 | 37459459.422 | kg/year | Calculated
C_energy | 2.3259 | 2.3259 | 9.2492 | $ M NZD/year | Units adjusted
LCOH (Storage+production) | 13.2729 | 10.6995 | 7.6465 | $/kg_H_2 | 1 Million=1000000 NZD, Units adjusted
LCOH (Storage only) | 2.4295 | 2.2163 | 0.73022 | $/kg_H_2
Scenario description
Three scenarios are developed reflecting the range of plausible outcomes for the Ahuroa UHS facility. The Conservative scenario applies a working gas capacity of 0.45 TWh with 15% equipment reusability (CDGR-equivalent) and current IEA (2024) electrolyser costs of USD 2,160/kWe. The Base Case uses the injection-rate-constrained hydrogen production of 10,572,240 kg/yr derived from AhuroaStorage.xlsx operational data (2020–2023) the binding physical constraint on annual H2 production at Ahuroa, with 60% equipment reusability per Deng et al. (2025) and current electrolyser costs. The Optimistic scenario applies the full theoretical working gas capacity of 1.40 TWh from Higgs et al. (2024), 70% equipment reusability, and IEA (2024) NZE 2030 projected electrolyser costs of USD 960/kWe, assuming infrastructure upgrades and future cost reductions.

## S8_Benchmark comparison
Comparison of obtained LCOH values with theoretical benchmarks
1. RESULTS OF THIS MODELLING FOR AHUROA UHS FACILITY
CONSERVATIVE | 13.2729 | Production + Storage | At top of MBIE near-term range (6-10). Higher due to lower equipment reusability and smaller working gas capacity.
BASE CASE | 10.7 | Production + Storage | Marginally above MBIE range. Original finding: injection rate is binding constraint not reservoir working gas volume.
OPTIMISTIC | 7.65 | Production + Storage | Within MBIE near-term range. Achievable with full capacity utilisation and 2030 electrolyser cost reductions.
BASE CASE (Storage only) | 2.42 | Storage only | For comparison with storage-only benchmarks. Consistent with Lord et al. (2014) and Yousefi et al. (2023).
CONSERVATIVE (Storage Only) | 2.21 | Storage only | For comparison with storage-only benchmarks. Consistent with Lord et al. (2014) and Yousefi et al. (2023).
BASE CASE (Storage only) | 0.73 | Storage only | For comparison with storage-only benchmarks. Consistent with Lord et al. (2014) and Yousefi et al. (2023).
2. New Zealand Benchmarks
Benchmark | NZD/kg | Scope | Geography | Year | Source
MBIE NZ green H2 near-term | 6 – 10 | Production only | New Zealand | 2022 | MBIE NZ Hydrogen Scenarios Report Sept 2022 p.41 ¦ Figure 5.2
MBIE NZ green H2 long-term 2050 | 2.87 – 3.73 | Production only | New Zealand | 2022 | MBIE NZ Hydrogen Scenarios Report Sept 2022 p.41 ¦ Figure 5.2
3. International benchmarks
Benchmark | NZD/kg | Scope | Geography | Original Value | Source
Lord et al. (2014) depleted reservoir | 3.23 (storage only) | Storage only | United States | USD 1.90/kg × 1.70 | Lord et al. (2014) Int. J. Hydrogen Energy 39(28) 15570-15582 p.8 ¦ Figure 3
Lord et al. (2014) inflation adjusted to 2025 | 3.56 (storage only) | Storage only | United States | USD 1.23/kg (2007 USD) × 1.03^18 × 1.70 | Lord et al. (2014) p.8 ¦ Figure 3 + CPI inflation 3%/yr
Yousefi et al. (2023) Dutch depleted gas field | 1.46 (storage only) | Storage only | Netherlands | EUR 0.79/kg × 1.85 | Yousefi et al. (2023) Int. J. Hydrogen Energy 48(74) 28824-28842 p.28831 ¦ Table 3
Yousefi et al. (2023) sensitivity range | 1.07 – 1.92 (storage only) | Storage only | Netherlands | EUR 0.58-1.04/kg × 1.85 | Yousefi et al. (2023) p.28831 ¦ Table 3 Sensitivity analysis

## S9_LCOH sensitivity
Sensitivity study of LCOH values based on other varying parameters
Parameter | Very Low | Low | Base | High | Stress | Unit | Notes/Source
1. Electricity Price | - | 70 | 100 | 150 | 250 | NZD/MWh | MBIE Dec 2023+EMI Marketing Data
LCOH Conservative (S+P) | - | 11.02 | 13.27 | 17.01 | 24.5 | NZD/MWh
LCOH Base(S+P) | - | 8.92 | 10.69 | 13.65 | 19.5 | NZD/MWh
LCOH Optimistic (S+P) | - | 5.87 | 7.64 | 10.6 | 16.5 | NZD/MWh
LCOH Conservative (S only) | - | 2.35 | 2.43 | 2.55 | 2.79 | NZD/MWh
LCOH Base(S only) | - | 2.14 | 2.21 | 2.33 | 2.58 | NZD/MWh
LCOH Optimistic (S only) | - | 0.66 | 0.73 | 0.85 | 1.1 | NZD/MWh
2. Discount Rate | - | 2 | 8 | 10 | - | % | NZ treasury Circular 2024/15, Page 2, SOC = 8% base and SRTP 2% sensitivity
LCOH Conservative | - | 11.55 | 13.27 | 13.94 | - | %
LCOH Base | - | 9.37 | 10.69 | 7.64 | - | %
LCOH Optimistic | - | 7.11 | 7.64 | 7.85 | - | %
3. Electrolyser Efficiency | - | 60 | 66 | 75 | - | % | -
LCOH Conservative | - | 14.35 | 13.27 | 11.97 | - | %
LCOH Base | - | 11.54 | 10.69 | 9.68 | - | %
LCOH Optimistic | - | 8.338 | 7.6 | 6.81 | - | %
4. Total Hours of Working (Capacity Factor) | 2600 | 4380 | 7000 | 8760 | - | hours/year | -
LCOH Conservative | 21.81 | 16.87 | 14.18 | 13.27 | - | hours/year
LCOH Base | 17.38 | 13.52 | 11.4 | 10.69 | - | hours/year
LCOH Optimistic | 10.61 | 8.9 | 7.96 | 7.6 | - | hours/year
5. Electrolyser CAPEX | - | 800 | 2160 | 3000 | - | USD/Kwe | -
LCOH Conservative | - | 11 | 13.27 | 14.67 | - | USD/Kwe
LCOH Base | - | 8.923 | 10.69 | 9.18 | - | USD/Kwe
LCOH Optimistic | - | 7.64 | 7.64 | 7.64 | - | USD/Kwe
6. H2 Loss rate | - | 0.5 | 1 | 2 | - | %/year | Pan et al. (2021),Page 6 diffusion loss
LCOH Conservative | - | 13.28 | 13.27 | 13.26 | - | %/year
LCOH Base | - | 10.64 | 10.69 | 10.8 | - | %/year
LCOH Optimistic | - | 7.6 | 7.6 | 7.72 | - | %/year

## S10_CCGT Assumptions
1. CCGT Equations & Assumptions
Equation ID | Formula | Explanation | Result Unit | Notes
EQ-CCGT-1 | Heat rate (GJ/MWh) = 3.6 ÷ η | η = CCGT thermal efficiency & unit conversion (1 MWh = 3.6 GJ) applied | GJ/MWh | Standard thermodynamic unit conversion
EQ-CCGT-2 | H2 consumption (kg/MWh) = 1,000 ÷ (LHV_H2 × η) | LHV_H2 = 33.3 kWh/kg, η = CCGT efficiency on hydrogen 1,000 = converts MWh to kWh | kg/MWh | Energy balance equation
EQ-CCGT-3 | Annual H2 demand (kg/yr) = Annual MWh × H2 consumption (kg/MWh) | Annual MWh = TCC annual generation from operational data | kg/yr | EQ-CCGT-2 applied to annual output
EQ-CCGT-4a | NG fuel cost (NZD/MWh) = NG price (NZD/GJ) × heat rate (GJ/MWh) | NG price = NZ wholesale gas price, Heat rate from EQ-CCGT-1 | NZD/MWh | -
EQ-CCGT-4b | H2 fuel cost (NZD/MWh) = LCOH (NZD/kg) × H2 consumption (kg/MWh) | LCOH from LCOH sheet (three scenarios), H2 consumption from EQ-CCGT-2 | NZD/MWh | links LCOH model to CCGT module
EQ-CCGT-5 | Fixed O&M per MWh = (Fixed O&M NZD/kW/yr × Capacity kW) ÷ Annual MWh | Fixed O&M rate from Garcia & Guédez Table B1, Capacity = TCC 383 MW = 383,000 kW | NZD/MWh | -
EQ-CCGT-6 | LCOE = Fuel cost + Fixed O&M/MWh + Variable O&M + Retrofit/MWh | Fuel cost from EQ-CCGT-4a or 4b, Retrofit/MWh = annualised retrofit ÷ annual MWh, Annualised retrofit = Retrofit CAPEX × CRF | NZD/MWh | Standard LCOE formula - Lord et al. 2014 structure
EQ-CCGT-7 | CRF = i(1+i)^n ÷ ((1+i)^n − 1) | i = discount rate (decimal), n = remaining plant life (years) | — | Standard capital recovery factor - NZ Treasury 2024/15
EQ-CCGT-8 | Cost gap (NZD/MWh) = LCOE_H2 − LCOE_NG | LCOE_H2 from EQ-CCGT-6 hydrogen scenario, LCOE_NG from EQ-CCGT-6 natural gas scenario | NZD/MWh | -
EQ-CCGT-9 | Carbon price breakeven (NZD/tCO2) = Cost gap ÷ CO2 factor_NG | CO2 factor_NG = 0.35 tCO2/MWh (natural gas CCGT emissions), CO2 factor_H2 = 0 (hydrogen is zero-carbon) | NZD/tCO2 | Garcia & Guédez p.9 Section 5.1 - CO2 factor
EQ-CCGT-10 | LCOE_NG_with_carbon = LCOE_NG + (CO2 factor × carbon price) | CO2 factor = 0.35 tCO2/MWh, Carbon price = NZ ETS price or sensitivity value | NZD/MWh | -
EQ-CCGT-11 | Ahuroa supply % of TCC demand = M_H2_effective ÷ Annual H2 demand × 100 | M_H2_effective from LCOH model (three scenarios), Annual H2 demand from EQ-CCGT-3 | % | -
2. TCC Plant Parameters (CCGT plant from Stratford Power Station)
TCC installed capacity | 383 | MW | MR2016 Monitoring Report - Contact Energy | Section 2.1 ¦ Process Description | -
TCC thermal efficiency (natural gas) | 0.567 | 56.7% | MR2016 Monitoring Report - Contact Energy | Section 2.1 ¦ Improved efficiency value | Design efficiency 56.0%. Improved efficiency 56.7% used as base case.
TCC thermal efficiency - hydrogen | 0.567 | 56.7% | Garcia & Guédez (2025) Table 2-3 pp.8-9 + stated assumption | Table A1 Appendix | Assumed equal to natural gas efficiency. Garcia & Guédez confirm 57-58% for comparable CCGT on H2.
TCC annual electricity generation | 1071000 | MWh/yr | power-technology.com - Taranaki Combined Cycle plant profile | Plant profile data | 1,071,000 MWh/year. Implied capacity factor = 1,071,000 / (383 × 8,760) = 31.9%.
TCC remaining plant life | 20 | years | MR2016 - commissioned 1998. CCGT design life 30-40 years. | Section 2.1 | 2025 − 1998 = 27 years operational. Assuming 20 years remaining to 2045. Conservative sensitivity: 10 years.
CO2 emissions factor - natural gas CCGT | 0.35 | tCO2/MWh | Garcia & Guédez (2025) Page 9 Section 5.1 | p.9 ¦ Section 5.1 | -
CO2 emissions factor - hydrogen CCGT | 0 | tCO2/MWh | Standard - hydrogen combustion produces water only | Physical chemistry - H2 + 0.5O2 → H2O | Zero direct CO2 emissions. Life-cycle emissions from green H2 production assumed zero when produced from renewable electricity.
3. Economic Parameters
Discount rate | 0.08 | 8% | EQ-CCGT-7 (CRF) | NZ Treasury Circular 2024/15 | p.2 ¦ Table of discount rates ¦ SOC commercial rate
EUR to NZD exchange rate | 1.85 | NZD/EUR | All EUR conversions | Reserve Bank of New Zealand | May 2025 market rate
4. O&M Parameters
CCGT fixed maintenance cost (EUR) | 13.4 | EUR/kW/year | Garcia & Guédez (2025) Table B1 Appendix B | Table B1, Appendix B Economic model
CCGT variable maintenance cost (EUR) | 2.42 | EUR/MWh | Garcia & Guédez (2025) Table B1 Appendix B | Table B1, Appendix B Economic model
CCGT H2 upgrade cost - >30% H2 volume (EUR) | 50 | EUR/kWel | Garcia & Guédez (2025) Table B1 Appendix B | Table B1, Row: CCGT upgrade specific cost >30%vol
5. Fuel Parameters
H2 lower heating value (LHV) | 33.3 | kWh/kg | Standard thermodynamic constant
NZ wholesale natural gas price - base case (2023) | 20 | NZD/GJ | MBIE NZ Energy Prices data 2024
NZ wholesale natural gas price - high sensitivity (2025) | 45 | NZD/GJ | EECA RETA Auckland Report (2025)
6. LCOH Values from LCOH modelling for Hydrogen storage and Production
LCOH - Conservative | 13.27 | NZD/kg H2
LCOH - Base Case | 10.7 | NZD/kg H2
LCOH - Optimistic | 7.65 | NZD/kg H2
M_H2 effective - Conservative | 9419866 | kg/yr
M_H2 effective - Base Case | 9419866 | kg/yr
M_H2 effective - Optimistic | 37459459 | kg/yr
A base-case natural gas price of NZD 20/GJ was adopted using historical industrial gas pricing data reported by the New Zealand Ministry of Business, Innovation and Employment (MBIE, 2024). High-price sensitivity cases of NZD 26–30/GJ and an LNG-import future scenario of NZD 45/GJ were adopted based on future gas market assumptions reported in the EECA RETA Auckland Report (2025, p.78).

## S11_CCGT Calculations
1. CCGT Calculations
Parameter | Value | Unit | Source
Capital Recovery Factor (CRF) | 0.10185 | - | NZ Treasury Circular 2024/15
Fixed O&M cost | 24.79 | NZD/kW/yr | Garcia & Guédez Table B1 & EUR rate: Reserve Bank NZ May 2025
Variable O&M cost | 4.477 | NZD/MWh | Garcia & Guédez Table B1 & EUR rate: Reserve Bank NZ May 2025
Retrofit CAPEX total | 35.4275 | NZD $M | Garcia & Guédez Table B1
Retrofit CAPEX annualised | 3.6084 | NZD $M/yr | EQ-CCGT-7 applied to retrofit CAPEX
Retrofit cost per MWh | 3.3692 | NZD/MWh | EQ-CCGT-6 component
Heat rate (GJ/MWh) | 6.3492 | GJ/MWh | EQ-CCGT-1 ¦ Standard thermodynamic conversion ¦ 1 MWh = 3.6 GJ
H2 consumption per MWh electricity | 52.963 | kg H2/MWh | EQ-CCGT-2
Annual H2 demand at TCC | 56723390.0567 | kg H2/yr | EQ-CCGT-3
Fixed O&M per MWh | 8.8651 | NZD/MWh | EQ-CCGT-5 ¦ Garcia & Guédez Table B1
2. LCOE Calulations
LCOE Component | Natural Gas | Hydrogen (Conservative) | Hydrogen (Base Case) | Hydrogen (Optimistic) | Unit | Source
Fuel cost per MWh | 126.9841 | 702.8192 | 566.7043 | 405.1671 | NZD/MWh | EQ-CCGT-4b from LCOH model
Fixed O&M per MWh | 8.8651 | 8.8651 | 8.8651 | 8.8651 | NZD/MWh | Garcia & Guédez Table B1 - Appendix B
Variable O&M | 4.477 | 4.477 | 4.477 | 4.477 | NZD/MWh | Garcia & Guédez Table B1 - Appendix B
Retrofit cost per MWh (H2 only - zero for NG) | 0 | 3.3692 | 3.3692 | 3.3692 | NZD/MWh | Garcia & Guédez Table B1 - EUR 50/kWel for >30%vol H2
LCOE (in NZD/MWh) | 140.3263 | 719.5305 | 583.4156 | 421.8784 | NZD/MWh | EQ-CCGT-6
LCOE (in NZD/KWh) | 0.14033 | 0.71953 | 0.58342 | 0.42188 | NZD/KWh

## S12_Cost competitiveness
COST COMPETITIVENESS ANALYSIS
Metric | Equation | Natural Gas | Conservative | Base Case | Optimistic | Unit | Source / Notes
Cost gap Hydrogen vs natural gas LCOE | EQ-CCGT-8: LCOE_H2 − LCOE_NG | - | 579.2043 | 443.0893 | 281.5521 | NZD/MWh | EQ-CCGT-8. Positive value = H2 electricity more expensive than NG.
Ahuroa H2 supply as % of TCC total demand | EQ-CCGT-11: M_H2_eff ÷ Annual H2 demand × 100 | - | 16.6067 | 16.6067 | 66.0388 | % | EQ-CCGT-11. KEY FINDING: Ahuroa can supply only ~16-66% of TCC's hydrogen demand during base and conservative scenarios. Ahuroa cannot fully fuel TCC at current injection-constrained capacity at base and conservative scenarios.
Carbon price needed to close cost gap | EQ-CCGT-9: Cost gap ÷ CO2 factor NG (27) | - | 1654.8693 | 1265.9694 | 804.4346 | NZD/tCO2 | EQ-CCGT-9. CO2 factor 0.35 tCO2/MWh: Garcia & Guédez p.9 S5.1. Current NZ ETS ~NZD 60-70/tCO2. Required carbon price is far above current levels.
Current NZ ETS carbon price (reference) | Reference only | 65 | - | - | - | NZD/tCO2 | NZ ETS approximate current price 2025.
NG LCOE including current NZ ETS carbon cost | EQ-CCGT-10: LCOE_NG + (CO2 factor × NZ ETS) | 163.0763 | - | - | - | NZD/MWh | EQ-CCGT-10 ¦ NZ ETS adds NZD 22.75/MWh to NG electricity cost
The carbon price required to make hydrogen-fuelled electricity from Ahuroa cost-competitive with natural gas generation at the Taranaki Combined Cycle plant ranges from NZD 998/tCO2 in the optimistic scenario to NZD 1,849/tCO2 in the conservative scenario. This is calculated by dividing the cost gap between hydrogen and natural gas LCOE by the natural gas CO2 emissions factor of 0.35 tCO2/MWh (Garcia and Guédez, 2025, p.9) , the logic being that a rising carbon price increases the cost of natural gas electricity while leaving hydrogen LCOE unchanged, since hydrogen combustion produces zero direct CO2 emissions. The current NZ ETS carbon price fluctuates between NZD 50–70/tCO2 (ICAP, 2025), with the 2026 auction reserve price floor set at NZD 71/tCO2 ,approximately 14–28 times lower than the breakeven price required across the three scenarios. This confirms that carbon pricing alone under current and near-term NZ policy settings is insufficient to make Ahuroa hydrogen commercially competitive with natural gas generation, and that competitiveness requires a combination of declining electrolyser costs, rising natural gas prices, and direct production support mechanisms beyond the existing ETS framework.

## S13_CCGT Sensitivity
Sensitivity Analysis - CCGT
1. Variation of parameters with variation in Natural Gas Prices
NG Price (NZD/GJ) | LCOE_NG (NZD/MWh) | LCOE_H2 Base (NZD/MWh) | Cost Gap (NZD/MWh) (Base Case) | Cost Gap (NZD/MWh) (Optimistic Case) | Carbon Price Breakeven (NZD/tCO2) (Base Case) | Carbon Price Breakeven (NZD/tCO2) (Optimistic Case) | NG LCOE including current NZ ETS carbon cost
12 | 89.5326 | 583.4156 | 493.883 | 332.3458 | 1411.0942 | 949.5593 | 112.2826
15 | 108.5802 | 583.4156 | 474.8353 | 313.2981 | 1356.6724 | 895.1375 | 131.3302
20 | 140.3263 | 583.4156 | 443.0893 | 281.5521 | 1265.9694 | 804.4346 | 163.0763
25 | 172.0723 | 583.4156 | 411.3433 | 249.8061 | 1175.2665 | 713.7316 | 194.8223
30 | 203.8183 | 583.4156 | 379.5972 | 218.06 | 1084.5635 | 623.0287 | 226.5683
35 | 235.5644 | 583.4156 | 347.8512 | 186.314 | 993.8606 | 532.3257 | 258.3144
40 | 267.3104 | 583.4156 | 316.1052 | 154.568 | 903.1576 | 441.6228 | 290.0604
2. Retrofit Cost
Retrofit Cost (EUR/kWel) | Total NZD $M | Retrofit per MWh (NZD) | LCOE_H2 Conservative (NZD/MWh) | LCOE_H2 Base (NZD/MWh) | LCOE_H2 Optimistic (NZD/MWh) | Cost Gap (NZD/MWh) (Conservative Case) | Cost Gap (NZD/MWh) (Base Case) | Cost Gap (NZD/MWh) (Optimistic Case) | Carbon Price Breakeven (NZD/tCO2) (Conservative Case) | Carbon Price Breakeven (NZD/tCO2) (Base Case) | Carbon Price Breakeven (NZD/tCO2) (Optimistic Case)
30 | 21.2565 | 2.0215 | 718.1829 | 582.0679 | 420.5307 | 577.8566 | 441.7416 | 280.2044 | 1651.0188 | 1262.119 | 800.5841
50 | 35.4275 | 3.3692 | 719.5305 | 583.4156 | 421.8784 | 579.2043 | 443.0893 | 281.5521 | 1654.8693 | 1265.9694 | 804.4346
80 | 56.684 | 5.3907 | 721.552 | 585.4371 | 423.8999 | 581.2257 | 445.1108 | 283.5736 | 1660.645 | 1271.7451 | 810.2103
3. Remaining Plant Life
Remaining Life (years) | CRF | Retrofit per MWh (NZD) | LCOE_H2 Conservative (NZD/MWh) | LCOE_H2 Base (NZD/MWh) | LCOE_H2 Optimistic (NZD/MWh) | Cost Gap (NZD/MWh) (Conservative Case) | Cost Gap (NZD/MWh) (Base Case) | Cost Gap (NZD/MWh) (Optimistic Case) | Carbon Price Breakeven (NZD/tCO2) (Conservative Case) | Carbon Price Breakeven (NZD/tCO2) (Base Case) | Carbon Price Breakeven (NZD/tCO2) (Optimistic Case)
10 | 0.149 | 4.9297 | 721.0911 | 584.9761 | 423.4389 | 580.7648 | 444.6499 | 283.1127 | 1659.3281 | 1270.4282 | 808.8934
15 | 0.1168 | 3.8646 | 720.026 | 583.911 | 422.3738 | 579.6997 | 443.5847 | 282.0475 | 1656.2848 | 1267.385 | 805.8501
20 | 0.1019 | 3.3692 | 719.5305 | 583.4156 | 421.8784 | 579.2043 | 443.0893 | 281.5521 | 1654.8693 | 1265.9694 | 804.4346
4. CCGT efficiency on Hydrogen
H2 Efficiency (%) | H2 consumption (kg/MWh) | H2 Fuel cost (NZD/MWh) | LCOE_H2 Conservative (NZD/MWh) | LCOE_H2 Base (NZD/MWh) | LCOE_H2 Optimistic (NZD/MWh) | Cost Gap (NZD/MWh) (Conservative Case) | Cost Gap (NZD/MWh) (Base Case) | Cost Gap (NZD/MWh) (Optimistic Case) | Carbon Price Breakeven (NZD/tCO2) (Conservative Case) | Carbon Price Breakeven (NZD/tCO2) (Base Case) | Carbon Price Breakeven (NZD/tCO2) (Optimistic Case)
55% | 54.6001 | 584.2206 | 741.254 | 600.9319 | 434.4017 | 600.9278 | 460.6056 | 294.0754 | 1716.9364 | 1316.016 | 840.2156
56% | 53.6251 | 573.7881 | 728.3158 | 590.4994 | 426.943 | 587.9895 | 450.1731 | 286.6167 | 1679.97 | 1286.2089 | 818.9048
58% | 51.7759 | 554.0023 | 703.7777 | 570.7136 | 412.797 | 563.4514 | 430.3873 | 272.4708 | 1609.8612 | 1229.678 | 778.4879
5. LCOH Scenario Impact on LCOE and Carbon Price Breakeven
LCOH Scenario | LCOH (NZD/kg) | H2 Fuel cost (NZD/MWh) | LCOE_H2 (NZD/MWh) | Cost Gap (NZD/MWh) | Carbon Price Breakeven(NZD/tCO2)
Conservative | 13.27 | 702.8192 | 719.5305 | 579.2043 | 1654.8693
Base | 10.7 | 566.7043 | 583.4156 | 443.0893 | 1265.9694
Optimistic | 7.65 | 405.1671 | 421.8784 | 281.5521 | 804.4346
7. Variation in NZ ETS Carbon Price - Impact on NG LCOE and Cost Gap
NZ ETS Carbon Price (NZD/tCO2) | LCOE_NG incl. Carbon Cost (NZD/MWh)
65 | 163.0763
100 | 175.3263
150 | 192.8263
200 | 210.3263
300 | 245.3263
500 | 315.3263
1000 | 490.3263

## S14_LCOH Charts
Charts LCOH Analysis

## S15_CCGT Charts
Charts - CCGT integration

## S16_Chart Data LCOH
1. CAPEX Breakdown Chart table
Well infrastructure | 6.154 | $M NZD
Surface facilities | 13.923 | $M NZD
Cushion gas system | 32.8925 | $M NZD
Contigency | 5.9157 | $M NZD
Electrolyser Plant | 223.597 | $M NZD
Total | 282.4822 | $M NZD
2. OPEX Breakdown Chart Table
Production Costs | 2.2593 | $M NZD
UHS facility Operation | 4.057 | $M NZD
Equipment depreciation | 0.952 | $M NZD
Indirect Expenses | 6.052 | $M NZD
Annual Maintanance Cost | 6.7079 | $M NZD
Annual Electricity Cost | 53.3418 | $M NZD
Total | 73.37 | $M NZD
3. Sensitivity Tornado chart
Parameter | Low impact (Low-Base) | High Impact (High-Base) | Difference | Base | High | Low
Electricity price | -4.82 | 13.81 | 18.63 | 10.69 | 24.5 | 5.87
Capacity factor | -3.09 | 6.69 | 9.78 | 10.69 | 17.38 | 7.6
Electrolyser Efficiency | -3.88 | 0.85 | 4.73 | 10.69 | 11.54 | 6.81
Discount rate | -3.58 | 3.25 | 6.83 | 10.69 | 13.94 | 7.11
H_2 Loss rate | -3.09 | 0 | 3.09 | 10.69 | 10.69 | 7.6
Eletrolyser CAPEX | -3.05 | 0 | 3.05 | 10.69 | 10.69 | 7.64
4. Electricity Price vs LCOH Chart
Electricity Price | LCOH Conservative (S+P) | LCOH Base(S+P) | LCOH Optimistic (S+P)
70 | 11.02 | 8.92 | 5.87
100 | 13.27 | 10.69 | 7.64
150 | 17.01 | 13.65 | 10.6
250 | 24.5 | 19.5 | 16.5
NZD/MWh | NZD/MWh | NZD/MWh | NZD/MWh
5. Scenarios and LCOH
| Conservative | Base | Optimistic
LCOH (Storage+production) | 13.27 | 10.6995 | 7.6465
LCOH (Storage only) | 2.43 | 2.2163 | 0.73022
6. Benchmarks
Lord et al. (2014) depleted reservoir | 3.23 | Storage only | United States | 1.95 | Storage only
Lord et al. (2014) inflation adjusted to 2025 | 3.56 | Storage only | United States | 2.21 | Storage only
Yousefi et al. (2023) Dutch depleted gas field | 1.46 | Storage only | Netherlands | 0.73 | Storage only
Yousefi et al. (2023) sensitivity range | 1.07 – 1.92 | Storage only | Netherlands
|  | Lord et al.(2014) inflation adjusted to 2025 | Yousefi et al. (2023) | Yousefi et al. (2023) sensitivity range
Conservative | 2.43 | 3.56 | 1.46 | 1.07
Base | 2.21 | 3.56 | 1.46 | 1.51
Optimistic | 0.73 | 3.56 | 1.46 | 1.92

## S17_Chart Data CCGT
Chart 1 - LCOE and natural gas prices
NG Price (NZD/GJ) | LCOE_NG (NZD/MWh) | LCOE_H2 Conservative (NZD/MWh) | LCOE_H2 Base (NZD/MWh) | LCOE_H2 Optimistic (NZD/MWh)
12 | 89.5326 | 719.53 | 583.4156 | 421.88
15 | 108.5802 | 719.53 | 583.4156 | 421.88
20 | 140.3263 | 719.53 | 583.4156 | 421.88
25 | 172.0723 | 719.53 | 583.4156 | 421.88
30 | 203.8183 | 719.53 | 583.4156 | 421.88
35 | 235.5644 | 719.53 | 583.4156 | 421.88
40 | 267.3104 | 719.53 | 583.4156 | 421.88
Chart2 - How variation in Natural gas prices influences prices at which carbon rates becomes breakeven
NG Price (NZD/GJ) | Carbon Price Breakeven (NZD/tCO2) (Base Case) | Carbon Price Breakeven (NZD/tCO2) (Optimistic Case) | NG LCOE including current NZ ETS carbon cost
12 | 1411.0942 | 949.5593 | 112.2826
15 | 1356.6724 | 895.1375 | 131.3302
20 | 1265.9694 | 804.4346 | 163.0763
25 | 1175.2665 | 713.7316 | 194.8223
30 | 1084.5635 | 623.0287 | 226.5683
35 | 993.8606 | 532.3257 | 258.3144
40 | 903.1576 | 441.6228 | 290.0604
Chart 3 - Would increasing Carbon pricing makes project more feasible?
NZ ETS Carbon Price (NZD/tCO2) | LCOE_NG incl. Carbon Cost (NZD/MWh) | LCOE_H2 Conservative (NZD/MWh) | LCOE_H2 Base (NZD/MWh) | LCOE_H2 Optimistic (NZD/MWh)
65 | 163.0763 | 719.53 | 583.4156 | 421.88
100 | 175.3263 | 719.53 | 583.4156 | 421.88
150 | 192.8263 | 719.53 | 583.4156 | 421.88
200 | 210.3263 | 719.53 | 583.4156 | 421.88
300 | 245.3263 | 719.53 | 583.4156 | 421.88
500 | 315.3263 | 719.53 | 583.4156 | 421.88
1000 | 490.3263 | 719.53 | 583.4156 | 421.88
0
Parameter | Low-Base | High-Base | Difference | Base | Low | High
LCOH (NZD/kg) | -161.5356 | 136.1144 | 297.65 | 583.4156 | 421.88 | 719.53
H2 Efficiency (%) | -12.7056 | 17.5144 | 30.22 | 583.4156 | 570.71 | 600.93
Remaining Plant Life (yr) | 0.0044 | 1.5644 | 1.56 | 583.4156 | 583.42 | 584.98
Retrofit Cost (EUR/kWel) | 2.0244 | -1.3456 | -3.37 | 583.4156 | 585.44 | 582.07
Chart 4-Ahuroa H2 supply as % of TCC total demand
Scenario | Ahuroa H2 supply as % of TCC total demand
Base | 16.6067
Optimistic | 66.0388
Chart 5 - Final LCOE and LCOH
Scenario | LCOH (NZD/kg) | LCOE_H2 (NZD/MWh) | Natural gas LCOE including current NZ ETS carbon cost (NZD/MWh)
Conservative | 13.27 | 719.5305 | 163.08
Base | 10.7 | 583.4156 | 163.08
Optimistic | 7.65 | 421.8784 | 163.08