## 1. Five-Step Model
P2H2P TECHNO-ECONOMIC MODEL
Supplementary Calculation Spreadsheet
A. CORE INPUT PARAMETERS
Parameter | Value | Unit
Dry-season electricity import deficit | 1765 | GWh / year
Wet-season surplus hydropower cap | 2 | GW
Wet-season production window | 4320 | hours (6 months × 30 days × 24 hrs)
Electrolyser energy requirement (PEM, BOL) | 55 | kWh / kg H₂
H₂ Lower Heating Value (LHV) | 33.33 | kWh / kg H₂
Fuel cell reconversion efficiency — baseline | 50% | decimal (50%) (PEMFC)
H₂ production cost — Scenario 1 (optimistic) | 1.24 | USD / kg H₂
H₂ production cost — Scenario 2 (conservative) | 3.4 | USD / kg H₂
Dry-season import price benchmark | 0.11 | USD / kWh
B. FIVE-STEP SEQUENTIAL CALCULATION (variable production cost only)
Step | Result | Unit
Step 1 — Energy required in H₂ form | 3530 | GWh
Step 2 — Total H₂ mass to produce | 105910591.0591 | kg H₂
Step 3a — Required production rate | 24516.3405 | kg H₂ / hour
Step 3b — Required electrolyser capacity | 1.3484 | GW
Step 4 — Electricity output per kg H₂ | 16.665 | kWh / kg H₂
Step 5a — Output price, Scenario 1 (optimistic) | 0.074407 | USD / kWh
Step 5b — Output price, Scenario 2 (conservative) | 0.20402 | USD / kWh
Saving vs. import benchmark — Scenario 1 (variable cost) | 32.36% | % saving
Premium vs. import benchmark — Scenario 2 (variable cost) | 85.47% | % premium
Annual financial saving — Scenario 1 (variable cost only) | 62820867.0867 | USD / year
25-year cumulative saving — Scenario 1 (undiscounted) | 1570521677.1677 | USD

## 2. Full LCOE
FULL LEVELISED COST OF ELECTRICITY (LCOE) — BASELINE (50% PEMFC efficiency)
Fuel cell and storage CAPEX annualised using Capital Recovery Factor (CRF) (Discount rate 7% ; Lifetime 20 years)
Parameter | Scenario 1 (Optimistic) | Scenario 2 (Conservative) | Unit
A. CAPITAL COST ASSUMPTIONS AND CRF CALCULATION
Discount rate | 7% | 7% | decimal (7%)
Project lifetime | 20 | 20 | years
Capital Recovery Factor (CRF) | 0.094393 | 0.094393 | decimal
Fuel cell plant CAPEX | 1352 | 1352 | USD / kW
Fuel cell average output capacity | 408.5648 | 408.5648 | MW
Fuel cell CAPEX — total investment | 552379629.6296 | 552379629.6296 | USD
Fuel cell CAPEX — annualised | 52140729.3617 | 52140729.3617 | USD / year
Fuel cell CAPEX — per kWh output | 0.029541 | 0.029541 | USD / kWh
H₂ storage CAPEX (underground salt cavern) | 2.3 | 2.3 | USD / kg H₂
H₂ storage volume (from Step 2, Sheet 1) | 105910591.0591 | 105910591.0591 | kg H₂
H₂ storage CAPEX — total investment | 243594359.4359 | 243594359.4359 | USD
H₂ storage CAPEX — annualised | 22993584.2817 | 22993584.2817 | USD / year
H₂ storage CAPEX — per kWh output | 0.013028 | 0.013028 | USD / kWh
B. FULL LCOE BUILD-UP (USD / kWh)
Line Item | Scenario 1 | Scenario 2 | Unit
Variable H₂ production cost | 0.074407 | 0.20402 | USD / kWh
Fuel cell CAPEX per kWh | 0.029541 | 0.029541 | USD / kWh
H₂ storage CAPEX per kWh | 0.013028 | 0.013028 | USD / kWh
FULL LCOE | 0.11698 | 0.24659 | USD / kWh
Import price benchmark | 0.11 | 0.11 | USD / kWh
Full LCOE premium vs. import price | 6.342% | 124.2% | % above import

## 3. Sensitivity Analysis
SENSITIVITY ANALYSIS — VARIABLE COST AND FULL LCOE
Section A: H₂ production cost is varied — one output price column (no Sc1/Sc2 split — they are identical when H₂ cost is the variable)
Section B: Fuel cell efficiency is varied — storage CAPEX recalculated for actual H₂ volume needed at each efficiency level
A. H₂ PRODUCTION COST SENSITIVITY (fuel cell efficiency fixed at 50% baseline)
H₂ Cost (USD/kg) | Variable Cost Output Price (USD/kWh) | Full LCOE (USD/kWh) | vs. Import Benchmark ($0.11/kWh) | Label
1 | 0.060006 | 0.10258 | -6.75%
1.24 | 0.074407 | 0.11698 | 6.342% | Scenario 1 baseline (Roadmap optimistic, $10/MWh electricity)
1.5 | 0.090009 | 0.13258 | 20.53%
1.83 | 0.10981 | 0.15238 | 38.53% | Variable-cost break-even: output price = $0.11/kWh import price
2 | 0.12001 | 0.16258 | 47.8%
3.4 | 0.20402 | 0.24659 | 124.2% | Scenario 2 baseline (Roadmap conservative, $60/MWh electricity)
B. FUEL CELL EFFICIENCY SENSITIVITY (H₂ cost fixed at $1.24/kg — Scenario 1)
FC Efficiency | kWh / kg H₂ output | Variable Cost (USD/kWh) [$1.24/kg] | H₂ Volume Needed (tonnes) | Storage CAPEX/kWh (recalculated) | Fuel Cell CAPEX /kWh (fixed) | Full LCOE (USD/kWh) | vs. Import / Technology Note
40% | 13.332 | 0.093009 | 132388.2388 | 0.016284 | 0.029541 | 0.13884 | Pessimistic PEMFC ¦ Full LCOE above import price
50% | 16.665 | 0.074407 | 105910.5911 | 0.013028 | 0.029541 | 0.11698 | Baseline PEMFC (Staffell et al. 2019) Full LCOE marginally above import price
60% | 19.998 | 0.062006 | 88258.8259 | 0.010856 | 0.029541 | 0.1024 | Optimistic SOFC Only scenario where Full LCOE < import price
C. VARIABLE-COST BREAK-EVEN
Break-even H₂ cost (variable cost = $0.11/kWh import price) |  | 1.8331 | USD / kg H₂
% above Scenario 1 baseline ($1.24/kg) |  | 47.83% | %
Full LCOE break-even (Full LCOE = $0.11/kWh import price) |  | 1.1237 | USD / kg H₂

## 4. Financial Impact
FINANCIAL IMPACT — SCENARIO 1, VARIABLE COST BASIS
Variable production cost saving only does not include full LCOE capital cost impact (see Sheet 2)
Metric | Value | Unit
Annual import volume | 1765 | GWh / year
Import price benchmark | 0.11 | USD / kWh
P2H2P variable output price — Scenario 1 | 0.074407 | USD / kWh
Variable cost saving per kWh — Scenario 1 | 0.035593 | USD / kWh
Annual financial saving — Scenario 1 | 62820867.0867 | USD / year
25-year cumulative saving — Scenario 1 (undiscounted) | 1570521677.1677 | USD